## Summary
beech-emitter-physics-mystery
Beech's distribution loop on 2026-01-24, when the pump's 0-10 V output was stepped by hand with the downstairs zone calling: each step over its counted minutes, the minute trace under the steps, the season's steady hours for comparison, the upstairs calls whose recovery sets the ten-minute exclusion, and the hourly records. Every cell is one number; the README in the experiments folder says how each table was made.
Tab | What the rows are | Rows | Columns | Produced by
beech-2026-01-24-steps | Beech 2026-01-24: each hand-set level of the pump's 0-10 V output over its counted samples (downstairs calling alone, both temperatures fresh within 90 s) | 5 | 14 | beech_jan24_steps.py
beech-2026-01-24-minutes | Beech 2026-01-24, 09:00 to 12:30 ET: the minute trace under the hand-set 0-10 V steps | 204 | 10 | pump_speed.py
beech-steady-drop | Beech steady-circulation hours by source temperature bin: drop quartiles, median flow, median heat | 5 | 9 | steady_drop.py
beech-cold-zone-events | beech: each idle-zone call inside a steady call, its recovery and the cold water it returned | 45 | 11 | bolus_recovery.py
emitter-theory-python | The paper's theory table computed in Python from the inputs on theory-inputs: the return each flow settles to under the emitter characteristic, the drop and heat that implies, against the measured heat | 4 | 6 | emitter_theory.py
stored-heat-python | The two fast steps' excess of measured over theory heat as heat stored in the iron, and the thermal mass that rise in return implies, computed in Python | 2 | 9 | emitter_theory.py
theory-inputs | The inputs every formula on the excel tabs reads; change one and the tabs follow | 8 | 3 | emitter_theory.py
emitter-theory-excel | The paper's theory table as formulas over theory-inputs: Return0F is the calibration return, each ReturnNF one iteration of R = S - K x ((S + R)/2 - room)^n / (500 x gpm); the last is the theory return | 4 | 14 | emitter_theory.py
stored-heat-excel | The two fast steps' stored heat and implied thermal mass as formulas over emitter-theory-excel | 2 | 9 | emitter_theory.py
beech-hourly | hw1.isone.me.versant.keene.beech.ta: one row per hour with enough valid samples, 2025-10-01 to 2026-05-01 | 4988 | 8 | emitter_drop.py

## beech-2026-01-24-steps
StartEt | EndEt | Volts | Gpm | HeldMin | CountedShare | SourceMeanF | SourceMinF | SourceMaxF | ReturnMeanF | ReturnMinF | ReturnMaxF | DropF | HeatKbtuPerH
09:35 | 09:53 | 3 | 1.77 | 18 | 0.25 | 155.8 | 153.9 | 157.3 | 132 | 131.6 | 132.2 | 23.8 | 21
10:03 | 10:15 | 10 | 4.45 | 12 | 1 | 145.8 | 125.7 | 166.6 | 132.5 | 124.8 | 141 | 13.3 | 29.6
10:23 | 10:53 | 8 | 4.12 | 30 | 0.67 | 172.9 | 160.8 | 180.8 | 154.7 | 150.1 | 158.6 | 18.3 | 37.6
10:55 | 11:03 | 3.5 | 1.98 | 8 | 0.98 | 167.8 | 165.4 | 172.1 | 146.4 | 142.5 | 149.8 | 21.4 | 21.2
11:22 | 11:45 | 6 | 3.16 | 23 | 0.53 | 170.8 | 159.3 | 180.3 | 150.8 | 147.4 | 154.2 | 20 | 31.6

## beech-2026-01-24-minutes
MinuteStartEt | MinuteStartS | Gpm | PumpW | Pump010V | SourceF | ReturnF | TempAgeS | zone1-down-whitewire-pwr | zone2-up-whitewire-pwr
2026-01-24 09:00 | 1769263200 | 2 | 7 | 3.5 | 154.52 | 129.39 | 47 | 1 | 0
2026-01-24 09:01 | 1769263260 | 2 | 7 | 3.5 | 155.27 | 129.93 | 39 | 1 | 0
2026-01-24 09:02 | 1769263320 | 2 | 7 | 3.5 | 154.45 | 130.48 | 37 | 1 | 0
2026-01-24 09:03 | 1769263380 | 2 | 7 | 3.5 | 152.77 | 131.21 | 40 | 1 | 0
2026-01-24 09:04 | 1769263440 | 2 | 7 | 3.5 | 152.39 | 131.63 | 60 | 1 | 0
2026-01-24 09:05 | 1769263500 | 2 | 7 | 3.5 | 152.2 | 131.83 | 70 | 1 | 0
2026-01-24 09:06 | 1769263560 | 2 | 7 | 3.5 | 151.93 | 131.86 | 107 | 1 | 0
2026-01-24 09:07 | 1769263620 | 2 | 7 | 3.5 | 151.68 | 131.73 | 147 | 1 | 0
2026-01-24 09:08 | 1769263680 | 2 | 7 | 3.5 | 151.43 | 131.34 | 73 | 1 | 0
2026-01-24 09:09 | 1769263740 | 2 | 7 | 3.5 | 151.13 | 131.09 | 83 | 1 | 0
2026-01-24 09:10 | 1769263800 | 2 | 7 | 3.5 | 150.88 | 130.74 | 56 | 1 | 0
2026-01-24 09:11 | 1769263860 | 2 | 7 | 3.5 | 150.72 | 130.62 | 87 | 1 | 0
2026-01-24 09:12 | 1769263920 | 2 | 7 | 3.5 | 150.48 | 130.37 | 79 | 1 | 0
2026-01-24 09:13 | 1769263980 | 2 | 7 | 3.5 | 150.48 | 130.19 | 139 | 1 | 0
2026-01-24 09:14 | 1769264040 | 2 | 7 | 3.5 | 150.22 | 130.01 | 159 | 1 | 0
2026-01-24 09:15 | 1769264100 | 2.008 | 7 | 3.5 | 150.05 | 129.75 | 96 | 1 | 0
2026-01-24 09:16 | 1769264160 | 2.01 | 7 | 3.5 | 150.04 | 129.33 | 107 | 1 | 0
2026-01-24 09:17 | 1769264220 | 2.01 | 7 | 3.5 | 149.85 | 129.09 | 137 | 1 | 0
2026-01-24 09:18 | 1769264280 | 2.01 | 7 | 3.5 | 149.67 | 128.97 | 98 | 1 | 0
2026-01-24 09:19 | 1769264340 | 2.01 | 7 | 3.5 | 149.49 | 128.97 | 158 | 1 | 0
2026-01-24 09:20 | 1769264400 | 2.01 | 9.2 | 3.5 | 149.28 | 128.88 | 168 | 1 | 0
2026-01-24 09:21 | 1769264460 | 2.01 | 7 | 3.5 | 149.27 | 128.86 | 107 | 1 | 0
2026-01-24 09:22 | 1769264520 | 2.01 | 7 | 3.5 | 149.27 | 128.86 | 167 | 1 | 0
2026-01-24 09:23 | 1769264580 | 2.01 | 7 | 3.5 | 149.15 | 128.86 | 227 | 1 | 0
2026-01-24 09:24 | 1769264640 | 2.01 | 7 | 3.5 | 148.91 | 128.86 | 287 | 1 | 0
2026-01-24 09:25 | 1769264700 | 2.01 | 7 | 3.5 | 148.9 | 128.5 | 84 | 1 | 0
2026-01-24 09:26 | 1769264760 | 2.01 | 7 | 3.5 | 148.89 | 128.5 | 107 | 1 | 0
2026-01-24 09:27 | 1769264820 | 2.01 | 7 | 3.5 | 148.89 | 128.5 | 167 | 1 | 0
2026-01-24 09:28 | 1769264880 | 2.507 | 7.7 | 3.5 | 148.89 | 125.73 | 227 | 1 | 1
2026-01-24 09:29 | 1769264940 | 3.153 | 9 | 3.5 | 148.89 | 109.72 | 287 | 1 | 1
2026-01-24 09:30 | 1769265000 | 3.182 | 9 | 3.5 | 148.79 | 105.4 | 297 | 1 | 1
2026-01-24 09:31 | 1769265060 | 3.18 | 9 | 3.5 | 148.77 | 112.45 | 107 | 1 | 1
2026-01-24 09:32 | 1769265120 | 3.18 | 9 | 3.5 | 152.66 | 118.12 | 127 | 1 | 1
2026-01-24 09:33 | 1769265180 | 3.18 | 8.7 | 3.5 | 134.24 | 120.11 | 16 | 1 | 1
2026-01-24 09:34 | 1769265240 | 2.987 | 8 | 3.5 | 148.14 | 122.54 | 7 | 1 | 0.667
2026-01-24 09:35 | 1769265300 | 1.77 | 6 | 3 | 155.95 | 124.62 | 27 | 1 | 0
2026-01-24 09:36 | 1769265360 | 1.76 | 6 | 3 | 157.14 | 125.08 | 47 | 1 | 0
2026-01-24 09:37 | 1769265420 | 1.76 | 6 | 3 | 157.26 | 126.73 | 96 | 1 | 0
2026-01-24 09:38 | 1769265480 | 1.76 | 6 | 3 | 157.32 | 126.6 | 146 | 1 | 0
2026-01-24 09:39 | 1769265540 | 1.76 | 6 | 3 | 157.64 | 127.27 | 69 | 1 | 0
2026-01-24 09:40 | 1769265600 | 1.76 | 6 | 3 | 157.68 | 129.24 | 79 | 1 | 0
2026-01-24 09:41 | 1769265660 | 1.76 | 6 | 3 | 157.69 | 130.68 | 107 | 1 | 0
2026-01-24 09:42 | 1769265720 | 1.76 | 6 | 3 | 157.69 | 131.38 | 167 | 1 | 0
2026-01-24 09:43 | 1769265780 | 1.76 | 6 | 3 | 157.51 | 131.76 | 197 | 1 | 0
2026-01-24 09:44 | 1769265840 | 1.76 | 6 | 3 | 157.33 | 132.12 | 81 | 1 | 0
2026-01-24 09:45 | 1769265900 | 1.76 | 6 | 3 | 157.27 | 132.22 | 91 | 1 | 0
2026-01-24 09:46 | 1769265960 | 1.76 | 6 | 3 | 157 | 132.24 | 107 | 1 | 0
2026-01-24 09:47 | 1769266020 | 1.76 | 6 | 3 | 156.6 | 132.24 | 167 | 1 | 0
2026-01-24 09:48 | 1769266080 | 1.76 | 6 | 3 | 156.21 | 132.24 | 227 | 1 | 0
2026-01-24 09:49 | 1769266140 | 1.76 | 6 | 3 | 155.83 | 132.24 | 287 | 1 | 0
2026-01-24 09:50 | 1769266200 | 1.768 | 6 | 3 | 155.28 | 132.06 | 297 | 1 | 0
2026-01-24 09:51 | 1769266260 | 1.77 | 6 | 3 | 154.72 | 132.03 | 107 | 1 | 0
2026-01-24 09:52 | 1769266320 | 1.77 | 6 | 3 | 154.16 | 131.65 | 54 | 1 | 0
2026-01-24 09:53 | 1769266380 | 1.77 | 6 | 3 | 153.73 | 131.46 | 84 | 1 | 0
2026-01-24 09:54 | 1769266440 | 2.23 | 10 | 4 | 153.29 | 131.14 | 69 | 1 | 0
2026-01-24 09:55 | 1769266500 | 2.707 | 14 | 5 | 153.12 | 131.21 | 47 | 1 | 0
2026-01-24 09:56 | 1769266560 | 2.785 | 15 | 5.17 | 153.61 | 132.23 | 67 | 1 | 0
2026-01-24 09:57 | 1769266620 | 3.522 | 26.2 | 6.83 | 153.95 | 133.85 | 89 | 1 | 0
2026-01-24 09:58 | 1769266680 | 3.89 | 33 | 7.5 | 153.62 | 135.85 | 119 | 1 | 0
2026-01-24 09:59 | 1769266740 | 4.257 | 43.8 | 8.33 | 151.31 | 137.77 | 10 | 1 | 0
2026-01-24 10:00 | 1769266800 | 4.347 | 46 | 8.5 | 148.77 | 138.47 | 47 | 1 | 0
2026-01-24 10:01 | 1769266860 | 4.483 | 47.5 | 9.33 | 147.36 | 137.93 | 57 | 1 | 0
2026-01-24 10:02 | 1769266920 | 4.488 | 47.7 | 9.5 | 146.18 | 136.64 | 29 | 1 | 0
2026-01-24 10:03 | 1769266980 | 4.38 | 47.3 | 10 | 148.87 | 135.46 | 13 | 1 | 0
2026-01-24 10:04 | 1769267040 | 4.38 | 47 | 10 | 145.99 | 135.37 | 31 | 1 | 0
2026-01-24 10:05 | 1769267100 | 4.455 | 47 | 10 | 144.03 | 135.31 | 29 | 1 | 0
2026-01-24 10:06 | 1769267160 | 4.47 | 47 | 10 | 142.34 | 134.38 | 19 | 1 | 0
2026-01-24 10:07 | 1769267220 | 4.47 | 48.3 | 10 | 141.88 | 132.98 | 13 | 1 | 0
2026-01-24 10:08 | 1769267280 | 4.47 | 48.7 | 10 | 131.29 | 131.69 | 43 | 1 | 0
2026-01-24 10:09 | 1769267340 | 4.47 | 49 | 10 | 131.47 | 128.79 | 27 | 1 | 0
2026-01-24 10:10 | 1769267400 | 4.453 | 49 | 10 | 139.7 | 125.16 | 21 | 1 | 0
2026-01-24 10:11 | 1769267460 | 4.45 | 49 | 10 | 150.72 | 125.21 | 49 | 1 | 0
2026-01-24 10:12 | 1769267520 | 4.45 | 49 | 10 | 157.25 | 129.72 | 6 | 1 | 0
2026-01-24 10:13 | 1769267580 | 4.45 | 49 | 10 | 152.44 | 136.26 | 4 | 1 | 0
2026-01-24 10:14 | 1769267640 | 4.45 | 49 | 10 | 164.09 | 139.6 | 16 | 1 | 0
2026-01-24 10:15 | 1769267700 | 4.442 | 49 | 10 | 166.68 | 142.11 | 27 | 1 | 0
2026-01-24 10:16 | 1769267760 | 5.733 | 54 | 9.83 | 163.4 | 140.31 | 3 | 1 | 1
2026-01-24 10:17 | 1769267820 | 5.968 | 37.5 | 7.17 | 150.29 | 120.58 | 8 | 1 | 1
2026-01-24 10:18 | 1769267880 | 5.87 | 35 | 7 | 143.71 | 129.53 | 22 | 1 | 1
2026-01-24 10:19 | 1769267940 | 4.168 | 15.3 | 4.67 | 144.81 | 129.65 | 42 | 1 | 1
2026-01-24 10:20 | 1769268000 | 2.833 | 7 | 3 | 150.6 | 128.6 | 44 | 1 | 1
2026-01-24 10:21 | 1769268060 | 3.03 | 9.7 | 3.67 | 157.27 | 126.88 | 10 | 1 | 0.667
2026-01-24 10:22 | 1769268120 | 3.943 | 35.8 | 7.67 | 152.44 | 128.88 | 6 | 1 | 0
2026-01-24 10:23 | 1769268180 | 4.1 | 39 | 8 | 159.5 | 132.13 | 11 | 1 | 0
2026-01-24 10:24 | 1769268240 | 4.1 | 39 | 8 | 162.84 | 138.05 | 6 | 1 | 0
2026-01-24 10:25 | 1769268300 | 4.125 | 39 | 8 | 148.87 | 141.64 | 14 | 1 | 0
2026-01-24 10:26 | 1769268360 | 4.13 | 39 | 8 | 151.38 | 142.86 | 45 | 1 | 0
2026-01-24 10:27 | 1769268420 | 4.13 | 39 | 8 | 158.22 | 140.27 | 7 | 1 | 0
2026-01-24 10:28 | 1769268480 | 4.13 | 39 | 8 | 163.51 | 139.47 | 37 | 1 | 0
2026-01-24 10:29 | 1769268540 | 4.13 | 39 | 8 | 170.29 | 142.67 | 9 | 1 | 0
2026-01-24 10:30 | 1769268600 | 4.107 | 39 | 8 | 173.65 | 146.71 | 11 | 1 | 0
2026-01-24 10:31 | 1769268660 | 4.11 | 39 | 8 | 176.47 | 150.88 | 6 | 1 | 0
2026-01-24 10:32 | 1769268720 | 4.11 | 39 | 8 | 178.91 | 154.4 | 13 | 1 | 0
2026-01-24 10:33 | 1769268780 | 4.11 | 39 | 8 | 177.22 | 156.96 | 23 | 1 | 0
2026-01-24 10:34 | 1769268840 | 4.12 | 39 | 8 | 168.31 | 158.44 | 38 | 1 | 0
2026-01-24 10:35 | 1769268900 | 4.13 | 39 | 8 | 163.35 | 157.52 | 14 | 1 | 0
2026-01-24 10:36 | 1769268960 | 4.13 | 39 | 8 | 169.75 | 153.74 | 4 | 1 | 0
2026-01-24 10:37 | 1769269020 | 4.13 | 39.8 | 8 | 177.88 | 151.36 | 26 | 1 | 0
2026-01-24 10:38 | 1769269080 | 4.13 | 40 | 8 | 179.83 | 152.94 | 43 | 1 | 0
2026-01-24 10:39 | 1769269140 | 4.13 | 40 | 8 | 173.3 | 156.94 | 5 | 1 | 0
2026-01-24 10:40 | 1769269200 | 4.12 | 40 | 8 | 163.75 | 158.55 | 40 | 1 | 0
2026-01-24 10:41 | 1769269260 | 4.12 | 40 | 8 | 163.65 | 155.81 | 13 | 1 | 0
2026-01-24 10:42 | 1769269320 | 4.12 | 40 | 8 | 173.11 | 151.71 | 6 | 1 | 0
2026-01-24 10:43 | 1769269380 | 4.12 | 40 | 8 | 179.73 | 150.81 | 46 | 1 | 0
2026-01-24 10:44 | 1769269440 | 4.12 | 40 | 8 | 178 | 154.29 | 5 | 1 | 0
2026-01-24 10:45 | 1769269500 | 4.1 | 40 | 8 | 168.43 | 157.82 | 14 | 1 | 0
2026-01-24 10:46 | 1769269560 | 4.1 | 40 | 8 | 161.71 | 157.71 | 34 | 1 | 0
2026-01-24 10:47 | 1769269620 | 4.1 | 39.2 | 8 | 167.85 | 153.73 | 4 | 1 | 0
2026-01-24 10:48 | 1769269680 | 4.1 | 39 | 8 | 176.8 | 150.58 | 16 | 1 | 0
2026-01-24 10:49 | 1769269740 | 4.1 | 39 | 8 | 180.43 | 151.99 | 22 | 1 | 0
2026-01-24 10:50 | 1769269800 | 4.12 | 39 | 8 | 178.52 | 154.65 | 50 | 1 | 0
2026-01-24 10:51 | 1769269860 | 4.12 | 39 | 8 | 178.52 | 154.65 | 110 | 1 | 0
2026-01-24 10:52 | 1769269920 | 4.12 | 39 | 8 | 178.52 | 154.65 | 170 | 1 | 0
2026-01-24 10:53 | 1769269980 | 4.12 | 39 | 8 | 178.52 | 154.65 | 230 | 1 | 0
2026-01-24 10:54 | 1769270040 | 2.687 | 12.3 | 3.5 | 176.15 | 151.59 | 250 | 1 | 0
2026-01-24 10:55 | 1769270100 | 1.98 | 7 | 3.5 | 170.93 | 149.79 | 50 | 1 | 0
2026-01-24 10:56 | 1769270160 | 1.98 | 7 | 3.5 | 169.61 | 149.66 | 90 | 1 | 0
2026-01-24 10:57 | 1769270220 | 1.98 | 7 | 3.5 | 168.49 | 148.6 | 23 | 1 | 0
2026-01-24 10:58 | 1769270280 | 1.98 | 7 | 3.5 | 167.92 | 147.34 | 35 | 1 | 0
2026-01-24 10:59 | 1769270340 | 1.98 | 7 | 3.5 | 167.37 | 145.93 | 45 | 1 | 0
2026-01-24 11:00 | 1769270400 | 1.98 | 7 | 3.5 | 166.83 | 144.48 | 29 | 1 | 0
2026-01-24 11:01 | 1769270460 | 1.98 | 7 | 3.5 | 166.34 | 143.37 | 41 | 1 | 0
2026-01-24 11:02 | 1769270520 | 1.98 | 7 | 3.5 | 165.56 | 142.69 | 31 | 1 | 0
2026-01-24 11:03 | 1769270580 | 1.98 | 7 | 3.5 | 164.6 | 142.05 | 35 | 1 | 0
2026-01-24 11:04 | 1769270640 | 2.58 | 13.5 | 5.17 | 161.96 | 141.57 | 41 | 1 | 0
2026-01-24 11:05 | 1769270700 | 3.163 | 20 | 6 | 159.1 | 141.52 | 39 | 1 | 0
2026-01-24 11:06 | 1769270760 | 3.163 | 20 | 6 | 152.61 | 142.3 | 27 | 1 | 0
2026-01-24 11:07 | 1769270820 | 3.17 | 20 | 6 | 156.67 | 142.66 | 79 | 1 | 0
2026-01-24 11:08 | 1769270880 | 3.17 | 20 | 6 | 156.97 | 142.66 | 139 | 1 | 0
2026-01-24 11:09 | 1769270940 | 3.17 | 20 | 6 | 156.97 | 142.66 | 199 | 1 | 0
2026-01-24 11:10 | 1769271000 | 3.17 | 20 | 6 | 156.97 | 142.66 | 259 | 1 | 0
2026-01-24 11:11 | 1769271060 | 3.17 | 20 | 6 | 156.97 | 142.66 | 319 | 1 | 0
2026-01-24 11:12 | 1769271120 | 3.17 | 20 | 6 | 156.97 | 142.66 | 379 | 1 | 0
2026-01-24 11:13 | 1769271180 | 3.17 | 20 | 6 | 156.97 | 142.66 | 439 | 1 | 0
2026-01-24 11:14 | 1769271240 | 3.17 | 20 | 6 | 156.97 | 142.66 | 499 | 1 | 0
2026-01-24 11:15 | 1769271300 | 3.17 | 20 | 6 | 156.97 | 142.66 | 559 | 1 | 0
2026-01-24 11:22 | 1769271720 | 5.15 | 24 | 6 | 158.61 | 140.78 | 9 | 1 | 1
2026-01-24 11:23 | 1769271780 | 3.475 | 20.7 | 6 | 157.64 | 144.15 | 47 | 1 | 0
2026-01-24 11:24 | 1769271840 | 3.14 | 20 | 6 | 158.33 | 144.29 | 82 | 1 | 0
2026-01-24 11:25 | 1769271900 | 3.157 | 20 | 6 | 173.24 | 142.91 | 14 | 1 | 0
2026-01-24 11:26 | 1769271960 | 3.16 | 20 | 6 | 175.5 | 143.3 | 34 | 1 | 0
2026-01-24 11:27 | 1769272020 | 3.16 | 20 | 6 | 165.94 | 146.09 | 5 | 1 | 0
2026-01-24 11:28 | 1769272080 | 3.16 | 20 | 6 | 159.04 | 149.28 | 19 | 1 | 0
2026-01-24 11:29 | 1769272140 | 3.16 | 20 | 6 | 163.88 | 149.6 | 23 | 1 | 0
2026-01-24 11:30 | 1769272200 | 3.152 | 20 | 6 | 171.63 | 147.18 | 10 | 1 | 0
2026-01-24 11:31 | 1769272260 | 3.15 | 20 | 6 | 177.4 | 146.19 | 48 | 1 | 0
2026-01-24 11:32 | 1769272320 | 3.15 | 20 | 6 | 178.9 | 148.13 | 22 | 1 | 0
2026-01-24 11:33 | 1769272380 | 3.15 | 20 | 6 | 170.75 | 151.69 | 8 | 1 | 0
2026-01-24 11:34 | 1769272440 | 3.15 | 20 | 6 | 160.72 | 153.8 | 20 | 1 | 0
2026-01-24 11:35 | 1769272500 | 3.158 | 20 | 6 | 163.37 | 152.94 | 30 | 1 | 0
2026-01-24 11:36 | 1769272560 | 3.16 | 20 | 6 | 171.37 | 149.74 | 7 | 1 | 0
2026-01-24 11:37 | 1769272620 | 3.16 | 20 | 6 | 177.86 | 147.63 | 36 | 1 | 0
2026-01-24 11:38 | 1769272680 | 3.16 | 20 | 6 | 179.15 | 148.59 | 46 | 1 | 0
2026-01-24 11:39 | 1769272740 | 3.16 | 20 | 6 | 170.73 | 152.05 | 5 | 1 | 0
2026-01-24 11:40 | 1769272800 | 3.177 | 20 | 6 | 160.81 | 154.03 | 30 | 1 | 0
2026-01-24 11:41 | 1769272860 | 3.18 | 20 | 6 | 163.58 | 153.1 | 40 | 1 | 0
2026-01-24 11:42 | 1769272920 | 3.18 | 20 | 6 | 172.31 | 149.87 | 6 | 1 | 0
2026-01-24 11:43 | 1769272980 | 3.18 | 20 | 6 | 178.83 | 147.77 | 33 | 1 | 0
2026-01-24 11:44 | 1769273040 | 3.18 | 20 | 6 | 178.85 | 148.87 | 43 | 1 | 0
2026-01-24 11:45 | 1769273100 | 3.163 | 20 | 6 | 170.15 | 152.36 | 7 | 1 | 0
2026-01-24 11:46 | 1769273160 | 3.16 | 20 | 6 | 161.61 | 154.1 | 46 | 1 | 0
2026-01-24 11:47 | 1769273220 | 3.16 | 20 | 6 | 165.58 | 153.06 | 56 | 1 | 0
2026-01-24 11:48 | 1769273280 | 3.16 | 20 | 6 | 174.06 | 150.07 | 8 | 1 | 0
2026-01-24 11:49 | 1769273340 | 3.16 | 20 | 6 | 179.94 | 148.4 | 42 | 1 | 0
2026-01-24 11:50 | 1769273400 | 1.05 | 6.7 | 6 | 178.15 | 149.52 | 12 | 0.333 | 0
2026-01-24 11:51 | 1769273460 | 0 | 0 | 6 | 173.38 | 147.11 | 7 | 0 | 0
2026-01-24 11:52 | 1769273520 | 0 | 0 | 6 | 169.91 | 144.6 | 13 | 0 | 0
2026-01-24 11:53 | 1769273580 | 0 | 0 | 6 | 167.1 | 142.92 | 15 | 0 | 0
2026-01-24 11:54 | 1769273640 | 0 | 0 | 6 | 164.55 | 141.31 | 13 | 0 | 0
2026-01-24 11:55 | 1769273700 | 0 | 0 | 6 | 162.91 | 140.58 | 61 | 0 | 0
2026-01-24 11:56 | 1769273760 | 0 | 0 | 6 | 162.91 | 140.58 | 121 | 0 | 0
2026-01-24 11:57 | 1769273820 | 0 | 0 | 6 | 162.91 | 140.58 | 181 | 0 | 0
2026-01-24 11:58 | 1769273880 | 0 | 0 | 6 | 162.91 | 140.58 | 241 | 0 | 0
2026-01-24 11:59 | 1769273940 | 0.663 | 2.7 | 4.33 | 165.23 | 136.72 | 281 | 0.333 | 0
2026-01-24 12:00 | 1769274000 | 1.998 | 8 | 3.5 | 169.95 | 127.76 | 50 | 1 | 0
2026-01-24 12:01 | 1769274060 | 2 | 8 | 3.5 | 169.97 | 131.17 | 110 | 1 | 0
2026-01-24 12:02 | 1769274120 | 2 | 8 | 3.5 | 169.97 | 136.28 | 170 | 1 | 0
2026-01-24 12:03 | 1769274180 | 2 | 8 | 3.5 | 170.21 | 139.76 | 190 | 1 | 0
2026-01-24 12:04 | 1769274240 | 2 | 7.7 | 3.5 | 170.33 | 141.5 | 95 | 1 | 0
2026-01-24 12:05 | 1769274300 | 1.988 | 7 | 3.5 | 170.13 | 142.32 | 105 | 1 | 0
2026-01-24 12:06 | 1769274360 | 1.98 | 7 | 3.5 | 165 | 142.71 | 63 | 1 | 0
2026-01-24 12:07 | 1769274420 | 1.98 | 7 | 3.5 | 160.76 | 143.01 | 65 | 1 | 0
2026-01-24 12:08 | 1769274480 | 1.32 | 4.7 | 3.5 | 160.02 | 142.6 | 75 | 0.667 | 0
2026-01-24 12:09 | 1769274540 | 0 | -1 | 3.5 | 158.13 | 140.36 | 10 | 0 | 0
2026-01-24 12:10 | 1769274600 | 0 | -1 | 3.5 | 155.39 | 137.67 | 10 | 0 | 0
2026-01-24 12:11 | 1769274660 | 0 | -1 | 3.5 | 153.02 | 135.7 | 13 | 0 | 0
2026-01-24 12:12 | 1769274720 | 0 | -1 | 3.5 | 151.2 | 134.2 | 14 | 0 | 0
2026-01-24 12:13 | 1769274780 | 0 | -0.8 | 3.5 | 149.23 | 132.75 | 15 | 0 | 0
2026-01-24 12:14 | 1769274840 | 0 | 0 | 3.5 | 147.43 | 131.5 | 19 | 0 | 0
2026-01-24 12:15 | 1769274900 | 0 | 0 | 3.5 | 145.77 | 130.17 | 20 | 0 | 0
2026-01-24 12:16 | 1769274960 | 0 | 0 | 3.5 | 144.05 | 128.97 | 17 | 0 | 0
2026-01-24 12:17 | 1769275020 | 0 | 0 | 3.5 | 142.45 | 127.65 | 15 | 0 | 0
2026-01-24 12:18 | 1769275080 | 0 | 0 | 3.5 | 140.93 | 126.65 | 21 | 0 | 0
2026-01-24 12:19 | 1769275140 | 0 | 0 | 3.5 | 139.39 | 125.6 | 20 | 0 | 0
2026-01-24 12:20 | 1769275200 | 0 | 0 | 3.5 | 137.96 | 124.71 | 30 | 0 | 0
2026-01-24 12:21 | 1769275260 | 0 | 0 | 3.5 | 136.66 | 123.82 | 21 | 0 | 0
2026-01-24 12:22 | 1769275320 | 0 | 0 | 3.5 | 135.2 | 122.67 | 21 | 0 | 0
2026-01-24 12:23 | 1769275380 | 0 | 0 | 3.5 | 133.88 | 121.73 | 22 | 0 | 0
2026-01-24 12:24 | 1769275440 | 0 | 0 | 3.5 | 132.59 | 120.71 | 18 | 0 | 0.667
2026-01-24 12:25 | 1769275500 | 1.508 | 7 | 3.5 | 148.73 | 99.16 | 24 | 0 | 1
2026-01-24 12:26 | 1769275560 | 1.51 | 7 | 3.5 | 162.93 | 77.29 | 10 | 0.5 | 1
2026-01-24 12:27 | 1769275620 | 3.118 | 9 | 3.5 | 164.68 | 92.76 | 24 | 1 | 1
2026-01-24 12:28 | 1769275680 | 3.14 | 9 | 3.5 | 164.98 | 103.93 | 79 | 1 | 1
2026-01-24 12:29 | 1769275740 | 3.14 | 9 | 3.5 | 164.92 | 110.87 | 129 | 1 | 1

## beech-steady-drop
System | SourceLoF | SourceHiF | Hours | DropQ25F | DropMedianF | DropQ75F | MedianGpm | MedianKwhPerH
beech | 60 | 70 | 21 | 0.5 | 0.6 | 0.7 | 3.16 | 0.3
beech | 130 | 140 | 29 | 15.8 | 17.1 | 17.7 | 2.1 | 5.18
beech | 140 | 150 | 47 | 19 | 19.8 | 21.2 | 2.1 | 6.11
beech | 150 | 160 | 53 | 21.2 | 23 | 24.4 | 2.1 | 7.1
beech | 160 | 170 | 24 | 24.2 | 25.5 | 26.5 | 2.05 | 7.69

## beech-cold-zone-events
CallStartEt | CallMinutes | PreDropF | PreSourceF | PostMinutes | RecoveryMin5Pct | RecoveryMin10Pct | PeakExcessF | SourceHeld | AddedGpm | SlugGal
2025-10-10 21:20 | 10 | 6.1 | 92.9 | 34 |  |  | 10.4 | FALSE | 1.93 | 0.4
2025-12-08 01:25 | 6 | 13.2 | 137.5 | 22 |  |  | 22.3 | FALSE | 0.97 | 8.8
2025-12-27 09:22 | 6 | 23.1 | 138.3 | 11 | 7 | 6 | 19.2 | FALSE | 0.73 | 2.3
2025-12-31 04:14 | 7 | 23.3 | 163.5 | 36 |  | 15 | 6.5 | FALSE | 0.91 | 9.1
2025-12-31 12:49 | 6 | 21.9 | 144.1 | 22 |  |  | 23.6 | FALSE | 0.99 | 2.9
2026-01-01 22:45 | 7 | 7.7 | 122.7 | 21 |  |  | 27.7 | FALSE | 0.94 | 5.6
2026-01-02 00:47 | 7 | 23.1 | 161.4 | 14 |  |  | 13.9 | FALSE | 0.93 | 7
2026-01-02 12:20 | 7 | 19.4 | 134.2 | 15 |  |  | 18.5 | FALSE | 0.88 | 2.5
2026-01-04 14:13 | 7 | 27.6 | 158.8 | 11 | 4 | 3 | 20 | FALSE | 0.84 | 3.2
2026-01-05 12:37 | 6 | 20 | 143.3 | 23 | 4 | 1 | 17.9 | FALSE | 1.04 | 4.5
2026-01-05 14:00 | 6 | 28.2 | 173.3 | 11 |  | 6 | 23.2 | TRUE | 0.83 | 4.5
2026-01-16 20:36 | 7 | 24.1 | 152.5 | 10 | 4 | 4 | 18.1 | FALSE | 0.89 | 4.2
2026-01-24 07:35 | 9 | 19.2 | 141.5 | 21 |  | 9 | 4.2 | FALSE | 0.96 | 8.7
2026-01-24 10:16 | 6 | 15.2 | 147.8 | 30 |  |  | 15.2 | FALSE | 0.14 | 2.2
2026-01-24 20:01 | 9 | 14.6 | 130.3 | 26 |  |  | 19.1 | FALSE | 0.91 | 9.2
2026-01-24 20:36 | 8 | 11 | 140.5 | 18 |  |  | 16.7 | FALSE | 0.96 | 10.1
2026-01-25 02:02 | 8 | 22.2 | 149.7 | 15 | 4 | 1 | 15.6 | TRUE | 1 | 5.2
2026-01-25 07:46 | 8 | 10.5 | 134.6 | 21 |  |  | 15.3 | FALSE | 1.03 | 11.2
2026-01-25 08:15 | 8 | 21.2 | 146.4 | 10 | 5 | 1 | 12.3 | TRUE | 1.04 | 4.6
2026-01-25 12:16 | 8 | 20.3 | 139.7 | 13 | 3 | 1 | 12.3 | TRUE | 0.95 | 4.1
2026-01-25 13:05 | 7 | 21.8 | 144.5 | 22 |  |  | 18.4 | FALSE | 1.02 | 3.4
2026-01-25 18:19 | 7 | 12.1 | 133.7 | 10 |  |  | 25.5 | FALSE | 0.96 | 4.5
2026-01-26 02:06 | 7 | 6.4 | 120.2 | 24 |  |  | 25.5 | FALSE | 0.96 | 5.8
2026-01-26 06:17 | 6 | 18.2 | 138.8 | 34 | 5 | 4 | 16.9 | FALSE | 1.06 | 4.2
2026-01-26 21:24 | 6 | 27.2 | 150.4 | 17 | 3 | 3 | 16 | FALSE | 0.97 | 2.3
2026-01-26 22:44 | 7 | 17.6 | 151.5 | 23 |  |  | 22.5 | FALSE | 0.91 | 6.4
2026-01-29 22:38 | 6 | 27.2 | 158.2 | 11 | 4 | 3 | 21.1 | FALSE | 1.04 | 3.1
2026-01-30 05:58 | 6 | 12.8 | 147.4 | 18 |  |  | 24.3 | FALSE | 1.09 | 8.1
2026-01-30 20:30 | 7 | 16 | 129.6 | 15 |  |  | 18.7 | FALSE | 0.97 | 2.9
2026-01-31 01:24 | 8 | 10.8 | 143 | 20 |  |  | 15.9 | FALSE | 0.89 | 11.8
2026-01-31 03:51 | 8 | 18.7 | 142.5 | 10 |  |  | 20.8 | FALSE | 0.87 | 3.4
2026-01-31 04:42 | 7 | 26.1 | 159.5 | 15 |  | 3 | 20 | FALSE | 0.92 | 3.4
2026-01-31 08:35 | 7 | 23.8 | 153 | 15 | 6 | 1 | 16.2 | FALSE | 0.9 | 3.3
2026-01-31 10:37 | 7 | 23.2 | 157.6 | 13 | 9 | 1 | 18.7 | FALSE | 0.93 | 4.9
2026-01-31 22:39 | 7 | 26.6 | 157.7 | 11 | 5 | 3 | 18.3 | FALSE | 0.91 | 3.3
2026-02-01 07:35 | 7 | 19.8 | 142.1 | 16 | 9 | 7 | 16.3 | FALSE | 0.99 | 3.2
2026-02-06 20:29 | 7 | 17.2 | 133.9 | 26 |  |  | 5.5 | FALSE | 0.83 | 7.5
2026-02-06 21:30 | 6 | 22.5 | 155.7 | 13 |  | 8 | 23.1 | FALSE | 0.99 | 4.4
2026-02-07 07:54 | 6 | 20.3 | 150.3 | 27 | 9 | 8 | 19.7 | FALSE | 0.95 | 4.8
2026-02-08 07:34 | 7 | 13.4 | 131.6 | 21 |  |  | 20.4 | FALSE | 0.83 | 4.2
2026-02-09 02:24 | 6 | 20.1 | 154.6 | 23 | 4 | 3 | 26.3 | FALSE | 0.99 | 5.6
2026-02-16 04:54 | 7 | 19.3 | 135.8 | 13 | 10 | 7 | 17.4 | FALSE | 0.85 | 2.6
2026-02-22 00:14 | 7 | 11.4 | 117.4 | 48 |  |  | 17.9 | FALSE | 1.01 | 3.2
2026-02-22 06:39 | 7 | 18.2 | 139.4 | 33 |  | 32 | 14.8 | FALSE | 1 | 6.3
2026-03-02 21:05 | 7 | 15.7 | 133.3 | 16 |  |  | 25.9 | FALSE | 0.93 | 2.6

## emitter-theory-python
Gpm | SourceF | TheoryReturnF | TheoryDropF | TheoryKbtuPerH | MeasuredKbtuPerH
1.98 | 168 | 146 | 22 | 21.8 | 21
3.16 | 171 | 155.9 | 15.1 | 23.9 | 32
4.12 | 173 | 160.9 | 12.1 | 25 | 38
infinite | 168 | 168 | 0 | 25.4

## stored-heat-python
Volts | ReturnStartF | ReturnEndF | MeasuredKbtuPerH | TheoryKbtuPerH | ExcessKbtuPerH | HeldMin | StoredKbtu | ImpliedMassBtuPerF
8 | 132 | 155 | 38 | 25 | 13 | 30 | 6.5 | 282
6 | 141 | 152 | 32 | 23.9 | 8.1 | 23 | 3.1 | 283

## theory-inputs
Input | Value | Unit
RoomF | 69 | F
Exponent | 1.3 | n in output = K x (mean water - room)^n
BtuPerHPerGpmF | 500 | water side: 8.33 lb/gal x 60 min/h x 1 BTU/lb F
CalibrationGpm | 1.98 | gpm, the 3.5 V step
CalibrationSourceF | 168 | F
CalibrationReturnF | 146 | F
CalibrationKbtuPerH |  | kBTU/h, from the three above
K |  | BTU/h per F^n, fixes the emitters

## emitter-theory-excel
Gpm | SourceF | Return0F | Return1F | Return2F | Return3F | Return4F | Return5F | Return6F | Return7F | TheoryReturnF | TheoryDropF | TheoryKbtuPerH | MeasuredKbtuPerH
1.98 | 168 | [11 empty] | 21
3.16 | 171 | [11 empty] | 32
4.12 | 173 | [11 empty] | 38
infinite | 168 | [9 empty] | 0

## stored-heat-excel
Volts | ReturnStartF | ReturnEndF | MeasuredKbtuPerH | TheoryKbtuPerH | ExcessKbtuPerH | HeldMin | StoredKbtu | ImpliedMassBtuPerF
8 | 132 | 155 |  |  |  | 30
6 | 141 | 152 |  |  |  | 23

## beech-hourly
HourStartEt | HourStartS | ValidFraction | FlowingFraction | MeanGpm | SourceF | ReturnF | HeatKwh
2025-10-01 11:00 | 1759330800 | 1 | 0.7194 | 1.999 | 61.72 | 61.02 | 0.205
2025-10-01 12:00 | 1759334400 | 1 | 0.3556 | 0.978 | 61.83 | 61.41 | 0.06
2025-10-01 13:00 | 1759338000 | 1 | 0 | 0 |  |  | 0
2025-10-01 14:00 | 1759341600 | 1 | 0 | 0 |  |  | 0
2025-10-01 15:00 | 1759345200 | 1 | 0 | 0 |  |  | 0
2025-10-01 16:00 | 1759348800 | 1 | 0 | 0 |  |  | 0
2025-10-01 17:00 | 1759352400 | 1 | 0 | 0 |  |  | 0
2025-10-01 18:00 | 1759356000 | 1 | 0.0778 | 0.292 | 61.31 | 59.57 | 0.075
2025-10-01 19:00 | 1759359600 | 1 | 0.1611 | 0.528 | 61.29 | 60.19 | 0.085
2025-10-01 20:00 | 1759363200 | 1 | 0.25 | 0.975 | 60.97 | 60.14 | 0.118
2025-10-01 21:00 | 1759366800 | 1 | 0.4694 | 1.523 | 60.61 | 59.96 | 0.147
2025-10-01 22:00 | 1759370400 | 1 | 1 | 4.387 | 60.42 | 59.95 | 0.304
2025-10-01 23:00 | 1759374000 | 1 | 1 | 5.626 | 60.28 | 59.86 | 0.344
2025-10-02 00:00 | 1759377600 | 1 | 1 | 5.9 | 60.12 | 59.7 | 0.363
2025-10-02 01:00 | 1759381200 | 1 | 1 | 5.898 | 59.96 | 59.55 | 0.353
2025-10-02 02:00 | 1759384800 | 1 | 1 | 5.9 | 59.8 | 59.33 | 0.409
2025-10-02 03:00 | 1759388400 | 0.95 | 1 | 5.899 | 59.6 | 59.17 | 0.354
2025-10-02 04:00 | 1759392000 | 1 | 1 | 5.902 | 59.42 | 59 | 0.363
2025-10-02 05:00 | 1759395600 | 1 | 1 | 5.902 | 59.24 | 58.8 | 0.381
2025-10-02 06:00 | 1759399200 | 1 | 1 | 5.898 | 59.06 | 58.61 | 0.382
2025-10-02 07:00 | 1759402800 | 1 | 1 | 5.902 | 58.77 | 58.33 | 0.38
2025-10-02 08:00 | 1759406400 | 1 | 1 | 5.901 | 58.6 | 58.17 | 0.377
2025-10-02 09:00 | 1759410000 | 1 | 1 | 5.903 | 58.44 | 58.03 | 0.359
2025-10-02 10:00 | 1759413600 | 1 | 1 | 5.902 | 58.32 | 57.92 | 0.348
2025-10-02 11:00 | 1759417200 | 1 | 1 | 5.898 | 58.25 | 57.86 | 0.331
2025-10-02 12:00 | 1759420800 | 0.9528 | 1 | 5.903 | 58.2 | 57.83 | 0.307
2025-10-02 13:00 | 1759424400 | 1 | 1 | 5.903 | 58.17 | 57.81 | 0.314
2025-10-02 14:00 | 1759428000 | 1 | 1 | 5.637 | 58.22 | 57.89 | 0.279
2025-10-02 15:00 | 1759431600 | 1 | 0.6722 | 3.205 | 58.31 | 57.98 | 0.155
2025-10-02 16:00 | 1759435200 | 1 | 0 | 0 |  |  | 0
2025-10-02 17:00 | 1759438800 | 1 | 0 | 0 |  |  | 0
2025-10-02 18:00 | 1759442400 | 1 | 0 | 0 |  |  | 0
2025-10-02 19:00 | 1759446000 | 1 | 0.0361 | 0.095 | 58.24 | 58.21 | 0
2025-10-02 20:00 | 1759449600 | 1 | 0.0556 | 0.154 | 58.01 | 58.29 | -0.006
2025-10-02 21:00 | 1759453200 | 1 | 0.1444 | 0.371 | 58.19 | 58.05 | 0.008
2025-10-02 22:00 | 1759456800 | 1 | 0.7556 | 2.174 | 58.31 | 57.96 | 0.113
2025-10-02 23:00 | 1759460400 | 0.95 | 1 | 2.78 | 58.33 | 58.01 | 0.125
2025-10-03 00:00 | 1759464000 | 1 | 1 | 2.779 | 58.38 | 58.05 | 0.136
2025-10-03 01:00 | 1759467600 | 1 | 1 | 2.902 | 58.38 | 58.03 | 0.149
2025-10-03 02:00 | 1759471200 | 0.9528 | 1 | 3.525 | 58.37 | 58.02 | 0.174
2025-10-03 03:00 | 1759474800 | 1 | 1 | 4.756 | 58.34 | 58.01 | 0.231
2025-10-03 04:00 | 1759478400 | 1 | 1 | 5.902 | 58.33 | 57.98 | 0.31
2025-10-03 05:00 | 1759482000 | 1 | 1 | 5.907 | 58.32 | 57.94 | 0.328
2025-10-03 06:00 | 1759485600 | 1 | 1 | 5.902 | 58.24 | 57.83 | 0.354
2025-10-03 07:00 | 1759489200 | 1 | 1 | 5.902 | 58.17 | 57.78 | 0.338
2025-10-03 08:00 | 1759492800 | 1 | 1 | 5.903 | 58.09 | 57.71 | 0.328
2025-10-03 09:00 | 1759496400 | 1 | 1 | 5.9 | 58.04 | 57.68 | 0.306
2025-10-03 10:00 | 1759500000 | 0.9528 | 1 | 5.902 | 58.01 | 57.65 | 0.297
2025-10-03 11:00 | 1759503600 | 1 | 1 | 5.359 | 58.05 | 57.69 | 0.286
2025-10-03 12:00 | 1759507200 | 1 | 0.4611 | 1.278 | 58.09 | 57.75 | 0.064
2025-10-03 13:00 | 1759510800 | 1 | 0 | 0 |  |  | 0
2025-10-03 14:00 | 1759514400 | 1 | 0 | 0 |  |  | 0
2025-10-03 15:00 | 1759518000 | 1 | 0 | 0 |  |  | 0
2025-10-03 16:00 | 1759521600 | 1 | 0 | 0 |  |  | 0
2025-10-03 17:00 | 1759525200 | 1 | 0 | 0 |  |  | 0
2025-10-03 18:00 | 1759528800 | 1 | 0 | 0 |  |  | 0
2025-10-03 19:00 | 1759532400 | 1 | 0 | 0 |  |  | 0
2025-10-03 20:00 | 1759536000 | 1 | 0 | 0 |  |  | 0
2025-10-03 21:00 | 1759539600 | 1 | 0 | 0 |  |  | 0
2025-10-03 22:00 | 1759543200 | 1 | 0 | 0 |  |  | 0
2025-10-03 23:00 | 1759546800 | 1 | 0 | 0 |  |  | 0
2025-10-04 00:00 | 1759550400 | 1 | 0 | 0 |  |  | 0
2025-10-04 01:00 | 1759554000 | 1 | 0 | 0 |  |  | 0
2025-10-04 02:00 | 1759557600 | 1 | 0 | 0 |  |  | 0
2025-10-04 03:00 | 1759561200 | 1 | 0.0028 | 0.007 | 58.55 | 57.96 | 0.001
2025-10-04 04:00 | 1759564800 | 1 | 0 | 0 |  |  | 0
2025-10-04 05:00 | 1759568400 | 1 | 0.0417 | 0.156 | 58.19 | 58.39 | -0.005
2025-10-04 06:00 | 1759572000 | 1 | 0.0861 | 0.235 | 58.15 | 58.58 | -0.015
2025-10-04 07:00 | 1759575600 | 1 | 0.0778 | 0.21 | 58.32 | 58.52 | -0.006
2025-10-04 08:00 | 1759579200 | 1 | 0.0028 | 0.008 | 58.28 | 58.21 | 0
2025-10-04 09:00 | 1759582800 | 1 | 0 | 0 |  |  | 0
2025-10-04 10:00 | 1759586400 | 1 | 0 | 0 |  |  | 0
2025-10-04 11:00 | 1759590000 | 1 | 0 | 0 |  |  | 0
2025-10-04 12:00 | 1759593600 | 1 | 0 | 0 |  |  | 0
2025-10-04 13:00 | 1759597200 | 1 | 0 | 0 |  |  | 0
2025-10-04 14:00 | 1759600800 | 1 | 0 | 0 |  |  | 0
2025-10-04 15:00 | 1759604400 | 1 | 0 | 0 |  |  | 0
2025-10-04 16:00 | 1759608000 | 0.9528 | 0 | 0 |  |  | 0
2025-10-04 17:00 | 1759611600 | 1 | 0 | 0 |  |  | 0
2025-10-04 18:00 | 1759615200 | 1 | 0 | 0 |  |  | 0
2025-10-04 19:00 | 1759618800 | 1 | 0 | 0 |  |  | 0
2025-10-04 20:00 | 1759622400 | 1 | 0 | 0 |  |  | 0
2025-10-04 21:00 | 1759626000 | 1 | 0 | 0 |  |  | 0
2025-10-04 22:00 | 1759629600 | 1 | 0 | 0 |  |  | 0
2025-10-04 23:00 | 1759633200 | 1 | 0 | 0 |  |  | 0
2025-10-05 00:00 | 1759636800 | 1 | 0 | 0 |  |  | 0
2025-10-05 01:00 | 1759640400 | 1 | 0 | 0 |  |  | 0
2025-10-05 02:00 | 1759644000 | 1 | 0 | 0 |  |  | 0
2025-10-05 03:00 | 1759647600 | 1 | 0 | 0 |  |  | 0
2025-10-05 04:00 | 1759651200 | 1 | 0 | 0 |  |  | 0
2025-10-05 05:00 | 1759654800 | 0.9528 | 0 | 0 |  |  | 0
2025-10-05 06:00 | 1759658400 | 1 | 0 | 0 |  |  | 0
2025-10-05 07:00 | 1759662000 | 1 | 0.0389 | 0.143 | 58.6 | 58.55 | 0.001
2025-10-05 08:00 | 1759665600 | 1 | 0 | 0 |  |  | 0
2025-10-05 09:00 | 1759669200 | 1 | 0 | 0 |  |  | 0
2025-10-05 10:00 | 1759672800 | 1 | 0 | 0 |  |  | 0
2025-10-05 11:00 | 1759676400 | 1 | 0 | 0 |  |  | 0
2025-10-05 12:00 | 1759680000 | 1 | 0 | 0 |  |  | 0
2025-10-05 13:00 | 1759683600 | 1 | 0 | 0 |  |  | 0
2025-10-05 14:00 | 1759687200 | 1 | 0 | 0 |  |  | 0
2025-10-05 15:00 | 1759690800 | 1 | 0 | 0 |  |  | 0
2025-10-05 16:00 | 1759694400 | 1 | 0 | 0 |  |  | 0
2025-10-05 17:00 | 1759698000 | 1 | 0 | 0 |  |  | 0
2025-10-05 18:00 | 1759701600 | 1 | 0 | 0 |  |  | 0
2025-10-05 19:00 | 1759705200 | 1 | 0 | 0 |  |  | 0
2025-10-05 20:00 | 1759708800 | 1 | 0 | 0 |  |  | 0
2025-10-05 21:00 | 1759712400 | 1 | 0 | 0 |  |  | 0
2025-10-05 22:00 | 1759716000 | 1 | 0 | 0 |  |  | 0
2025-10-05 23:00 | 1759719600 | 1 | 0 | 0 |  |  | 0
2025-10-06 00:00 | 1759723200 | 1 | 0 | 0 |  |  | 0
2025-10-06 01:00 | 1759726800 | 1 | 0 | 0 |  |  | 0
2025-10-06 02:00 | 1759730400 | 1 | 0 | 0 |  |  | 0
2025-10-06 03:00 | 1759734000 | 1 | 0 | 0 |  |  | 0
2025-10-06 04:00 | 1759737600 | 1 | 0 | 0 |  |  | 0
2025-10-06 05:00 | 1759741200 | 1 | 0 | 0 |  |  | 0
2025-10-06 06:00 | 1759744800 | 1 | 0 | 0 |  |  | 0
2025-10-06 07:00 | 1759748400 | 1 | 0 | 0 |  |  | 0
2025-10-06 08:00 | 1759752000 | 1 | 0 | 0 |  |  | 0
2025-10-06 09:00 | 1759755600 | 1 | 0 | 0 |  |  | 0
2025-10-06 10:00 | 1759759200 | 1 | 0 | 0 |  |  | 0
2025-10-06 11:00 | 1759762800 | 1 | 0 | 0 |  |  | 0
2025-10-06 12:00 | 1759766400 | 1 | 0 | 0 |  |  | 0
2025-10-06 13:00 | 1759770000 | 1 | 0 | 0 |  |  | 0
2025-10-06 14:00 | 1759773600 | 1 | 0 | 0 |  |  | 0
2025-10-06 15:00 | 1759777200 | 1 | 0 | 0 |  |  | 0
2025-10-06 16:00 | 1759780800 | 1 | 0 | 0 |  |  | 0
2025-10-06 17:00 | 1759784400 | 1 | 0 | 0 |  |  | 0
2025-10-06 18:00 | 1759788000 | 1 | 0 | 0 |  |  | 0
2025-10-06 19:00 | 1759791600 | 1 | 0 | 0 |  |  | 0
2025-10-06 20:00 | 1759795200 | 1 | 0 | 0 |  |  | 0
2025-10-06 21:00 | 1759798800 | 1 | 0 | 0 |  |  | 0
2025-10-06 22:00 | 1759802400 | 1 | 0 | 0 |  |  | 0
2025-10-06 23:00 | 1759806000 | 1 | 0 | 0 |  |  | 0
2025-10-07 00:00 | 1759809600 | 1 | 0 | 0 |  |  | 0
2025-10-07 01:00 | 1759813200 | 1 | 0 | 0 |  |  | 0
2025-10-07 02:00 | 1759816800 | 1 | 0 | 0 |  |  | 0
2025-10-07 03:00 | 1759820400 | 1 | 0 | 0 |  |  | 0
2025-10-07 04:00 | 1759824000 | 1 | 0 | 0 |  |  | 0
2025-10-07 05:00 | 1759827600 | 1 | 0 | 0 |  |  | 0
2025-10-07 06:00 | 1759831200 | 1 | 0 | 0 |  |  | 0
2025-10-07 07:00 | 1759834800 | 1 | 0 | 0 |  |  | 0
2025-10-07 08:00 | 1759838400 | 1 | 0 | 0 |  |  | 0
2025-10-07 09:00 | 1759842000 | 1 | 0 | 0 |  |  | 0
2025-10-07 10:00 | 1759845600 | 1 | 0 | 0 |  |  | 0
2025-10-07 11:00 | 1759849200 | 1 | 0 | 0 |  |  | 0
2025-10-07 12:00 | 1759852800 | 1 | 0 | 0 |  |  | 0
2025-10-07 13:00 | 1759856400 | 1 | 0 | 0 |  |  | 0
2025-10-07 14:00 | 1759860000 | 1 | 0 | 0 |  |  | 0
2025-10-07 15:00 | 1759863600 | 1 | 0 | 0 |  |  | 0
2025-10-07 16:00 | 1759867200 | 1 | 0 | 0 |  |  | 0
2025-10-07 17:00 | 1759870800 | 1 | 0 | 0 |  |  | 0
2025-10-07 18:00 | 1759874400 | 1 | 0 | 0 |  |  | 0
2025-10-07 19:00 | 1759878000 | 1 | 0 | 0 |  |  | 0
2025-10-07 20:00 | 1759881600 | 1 | 0 | 0 |  |  | 0
2025-10-07 21:00 | 1759885200 | 1 | 0 | 0 |  |  | 0
2025-10-07 22:00 | 1759888800 | 1 | 0 | 0 |  |  | 0
2025-10-07 23:00 | 1759892400 | 1 | 0 | 0 |  |  | 0
2025-10-08 00:00 | 1759896000 | 0.9972 | 0 | 0 |  |  | 0
2025-10-08 01:00 | 1759899600 | 1 | 0 | 0 |  |  | 0
2025-10-08 02:00 | 1759903200 | 1 | 0 | 0 |  |  | 0
2025-10-08 03:00 | 1759906800 | 1 | 0 | 0 |  |  | 0
2025-10-08 04:00 | 1759910400 | 1 | 0 | 0 |  |  | 0
2025-10-08 06:00 | 1759917600 | 1 | 0 | 0 |  |  | 0
2025-10-08 07:00 | 1759921200 | 1 | 0 | 0 |  |  | 0
2025-10-08 08:00 | 1759924800 | 1 | 0 | 0 |  |  | 0
2025-10-08 09:00 | 1759928400 | 1 | 0 | 0 |  |  | 0
2025-10-08 10:00 | 1759932000 | 1 | 0 | 0 |  |  | 0
2025-10-08 11:00 | 1759935600 | 1 | 0 | 0 |  |  | 0
2025-10-08 12:00 | 1759939200 | 1 | 0 | 0 |  |  | 0
2025-10-08 13:00 | 1759942800 | 1 | 0 | 0 |  |  | 0
2025-10-08 14:00 | 1759946400 | 1 | 0 | 0 |  |  | 0
2025-10-08 15:00 | 1759950000 | 1 | 0 | 0 |  |  | 0
2025-10-08 16:00 | 1759953600 | 1 | 0 | 0 |  |  | 0
2025-10-08 17:00 | 1759957200 | 1 | 0 | 0 |  |  | 0
2025-10-08 18:00 | 1759960800 | 1 | 0 | 0 |  |  | 0
2025-10-08 19:00 | 1759964400 | 1 | 0.0083 | 0.036 | 59.68 | 59.61 | 0
2025-10-08 20:00 | 1759968000 | 1 | 0 | 0 |  |  | 0
2025-10-08 21:00 | 1759971600 | 1 | 0 | 0 |  |  | 0
2025-10-08 22:00 | 1759975200 | 1 | 0 | 0 |  |  | 0
2025-10-08 23:00 | 1759978800 | 1 | 0 | 0 |  |  | 0
2025-10-09 00:00 | 1759982400 | 1 | 0 | 0 |  |  | 0
2025-10-09 01:00 | 1759986000 | 1 | 0 | 0 |  |  | 0
2025-10-09 02:00 | 1759989600 | 1 | 0.0222 | 0.082 | 59.11 | 58.54 | 0.007
2025-10-09 03:00 | 1759993200 | 1 | 0.0306 | 0.114 | 58.88 | 58.2 | 0.011
2025-10-09 05:00 | 1760000400 | 1 | 0.6139 | 2.821 | 58.68 | 58.29 | 0.162
2025-10-09 06:00 | 1760004000 | 1 | 0.9111 | 5.346 | 58.62 | 58.26 | 0.286
2025-10-09 07:00 | 1760007600 | 1 | 1 | 5.899 | 58.59 | 58.22 | 0.316
2025-10-09 08:00 | 1760011200 | 1 | 1 | 5.893 | 58.53 | 58.14 | 0.336
2025-10-09 09:00 | 1760014800 | 1 | 1 | 5.898 | 58.44 | 58.05 | 0.332
2025-10-09 10:00 | 1760018400 | 1 | 1 | 5.9 | 58.37 | 57.96 | 0.35
2025-10-09 11:00 | 1760022000 | 1 | 1 | 5.208 | 58.27 | 57.87 | 0.303
2025-10-09 12:00 | 1760025600 | 1 | 1 | 4.109 | 58.23 | 57.87 | 0.221
2025-10-09 13:00 | 1760029200 | 1 | 1 | 3.458 | 58.22 | 57.86 | 0.183
2025-10-09 14:00 | 1760032800 | 0.9528 | 1 | 2.779 | 58.22 | 57.89 | 0.127
2025-10-09 15:00 | 1760036400 | 1 | 0.9861 | 2.738 | 58.27 | 57.94 | 0.13
2025-10-09 17:00 | 1760043600 | 1 | 0.8333 | 2.725 | 58.19 | 57.81 | 0.149
2025-10-09 18:00 | 1760047200 | 1 | 0.9333 | 3.384 | 58.16 | 57.77 | 0.191
2025-10-09 19:00 | 1760050800 | 1 | 0.8972 | 3.412 | 58.16 | 57.83 | 0.165
2025-10-09 20:00 | 1760054400 | 1 | 1 | 5.052 | 58.19 | 57.84 | 0.261
2025-10-09 21:00 | 1760058000 | 1 | 1 | 5.898 | 58.16 | 57.81 | 0.302
2025-10-09 22:00 | 1760061600 | 1 | 1 | 5.9 | 58.18 | 57.8 | 0.324
2025-10-09 23:00 | 1760065200 | 0.9944 | 1 | 5.899 | 58.14 | 57.75 | 0.342
2025-10-10 00:00 | 1760068800 | 1 | 1 | 5.901 | 58.09 | 57.71 | 0.331
2025-10-10 01:00 | 1760072400 | 1 | 1 | 5.902 | 58.01 | 57.61 | 0.35
2025-10-10 02:00 | 1760076000 | 1 | 1 | 5.896 | 57.91 | 57.49 | 0.362
2025-10-10 03:00 | 1760079600 | 1 | 1 | 5.901 | 57.75 | 57.35 | 0.342
2025-10-10 04:00 | 1760083200 | 0.9528 | 1 | 5.901 | 57.62 | 57.21 | 0.333
2025-10-10 05:00 | 1760086800 | 1 | 1 | 5.9 | 57.49 | 57.05 | 0.375
2025-10-10 06:00 | 1760090400 | 1 | 1 | 5.902 | 57.3 | 56.88 | 0.364
2025-10-10 07:00 | 1760094000 | 1 | 1 | 5.902 | 57.14 | 56.7 | 0.377
2025-10-10 08:00 | 1760097600 | 1 | 1 | 5.901 | 56.95 | 56.54 | 0.357
2025-10-10 09:00 | 1760101200 | 1 | 1 | 5.899 | 56.81 | 56.41 | 0.346
2025-10-10 10:00 | 1760104800 | 1 | 1 | 5.896 | 56.7 | 56.31 | 0.339
2025-10-10 11:00 | 1760108400 | 1 | 1 | 5.893 | 56.62 | 56.26 | 0.312
2025-10-10 12:00 | 1760112000 | 0.9556 | 1 | 5.9 | 56.59 | 56.23 | 0.295
2025-10-10 13:00 | 1760115600 | 1 | 1 | 5.898 | 56.58 | 56.23 | 0.303
2025-10-10 14:00 | 1760119200 | 1 | 1 | 5.894 | 56.6 | 56.25 | 0.299
2025-10-10 15:00 | 1760122800 | 1 | 1 | 5.862 | 56.66 | 56.36 | 0.263
2025-10-10 16:00 | 1760126400 | 0.9528 | 1 | 5.906 | 56.78 | 56.46 | 0.263
2025-10-10 17:00 | 1760130000 | 0.9528 | 1 | 5.882 | 56.93 | 56.63 | 0.252
2025-10-10 18:00 | 1760133600 | 1 | 1 | 5.897 | 57.04 | 56.7 | 0.288
2025-10-10 19:00 | 1760137200 | 1 | 1 | 5.897 | 57.11 | 56.75 | 0.309
2025-10-10 20:00 | 1760140800 | 1 | 1 | 5.396 | 79.45 | 74.85 | 3.634
2025-10-10 21:00 | 1760144400 | 1 | 1 | 4.046 | 106.26 | 97.96 | 4.924
2025-10-10 22:00 | 1760148000 | 1 | 0.6389 | 2.351 | 142.76 | 128.23 | 5.004
2025-10-10 23:00 | 1760151600 | 1 | 0.2194 | 0.78 | 151.44 | 115.87 | 4.065
2025-10-11 00:00 | 1760155200 | 1 | 0.0861 | 0.309 | 137.2 | 107.46 | 1.348
2025-10-11 01:00 | 1760158800 | 1 | 0.1389 | 0.476 | 161.84 | 111.8 | 3.49
2025-10-11 02:00 | 1760162400 | 1 | 0.0806 | 0.296 | 155.97 | 107.34 | 2.097
2025-10-11 03:00 | 1760166000 | 1 | 0.0778 | 0.285 | 153.7 | 105 | 2.029
2025-10-11 06:00 | 1760176800 | 1 | 0.1111 | 0.375 | 147.04 | 100.73 | 2.532
2025-10-11 07:00 | 1760180400 | 1 | 0.0833 | 0.306 | 147.11 | 105.03 | 1.886
2025-10-11 08:00 | 1760184000 | 1 | 0.1444 | 0.468 | 149.57 | 104.91 | 3.043
2025-10-11 09:00 | 1760187600 | 0.9583 | 0 | 0 |  |  | 0
2025-10-11 10:00 | 1760191200 | 1 | 0 | 0 |  |  | 0
2025-10-11 11:00 | 1760194800 | 1 | 0.0611 | 0.156 | 117.46 | 72.54 | 1.026
2025-10-11 12:00 | 1760198400 | 1 | 0 | 0 |  |  | 0
2025-10-11 13:00 | 1760202000 | 1 | 0 | 0 |  |  | 0
2025-10-11 14:00 | 1760205600 | 1 | 0 | 0 |  |  | 0
2025-10-11 15:00 | 1760209200 | 1 | 0 | 0 |  |  | 0
2025-10-11 16:00 | 1760212800 | 1 | 0 | 0 |  |  | 0
2025-10-11 17:00 | 1760216400 | 1 | 0 | 0 |  |  | 0
2025-10-11 18:00 | 1760220000 | 1 | 0 | 0 |  |  | 0
2025-10-11 19:00 | 1760223600 | 1 | 0 | 0 |  |  | 0
2025-10-11 20:00 | 1760227200 | 1 | 0 | 0 |  |  | 0
2025-10-11 21:00 | 1760230800 | 1 | 0 | 0 |  |  | 0
2025-10-11 22:00 | 1760234400 | 1 | 0 | 0 |  |  | 0
2025-10-11 23:00 | 1760238000 | 1 | 0 | 0 |  |  | 0
2025-10-12 00:00 | 1760241600 | 1 | 0 | 0 |  |  | 0
2025-10-12 01:00 | 1760245200 | 1 | 0.0333 | 0.123 | 104.27 | 63.19 | 0.74
2025-10-12 02:00 | 1760248800 | 1 | 0.0861 | 0.314 | 113.26 | 84.68 | 1.317
2025-10-12 03:00 | 1760252400 | 1 | 0.0833 | 0.313 | 84.28 | 76.48 | 0.356
2025-10-12 04:00 | 1760256000 | 1 | 0.2806 | 0.973 | 83.48 | 76.44 | 1.002
2025-10-12 05:00 | 1760259600 | 1 | 0.4194 | 1.558 | 82.45 | 78.24 | 0.961
2025-10-12 06:00 | 1760263200 | 1 | 0.6917 | 2.486 | 81.55 | 78.21 | 1.217
2025-10-12 07:00 | 1760266800 | 1 | 1 | 3.912 | 79.31 | 77 | 1.325
2025-10-12 08:00 | 1760270400 | 1 | 1 | 3.926 | 76.91 | 74.79 | 1.219
2025-10-12 09:00 | 1760274000 | 0.95 | 1 | 3.94 | 75.07 | 73.21 | 1.023
2025-10-12 10:00 | 1760277600 | 0.9972 | 1 | 3.735 | 74.18 | 72.68 | 0.815
2025-10-12 11:00 | 1760281200 | 1 | 0.3806 | 1.412 | 73.16 | 71.66 | 0.311
2025-10-12 12:00 | 1760284800 | 1 | 0 | 0 |  |  | 0
2025-10-12 13:00 | 1760288400 | 0.9694 | 0 | 0 |  |  | 0
2025-10-12 14:00 | 1760292000 | 1 | 0 | 0 |  |  | 0
2025-10-12 15:00 | 1760295600 | 1 | 0 | 0 |  |  | 0
2025-10-12 16:00 | 1760299200 | 1 | 0 | 0 |  |  | 0
2025-10-12 17:00 | 1760302800 | 1 | 0.0472 | 0.177 | 72.34 | 61.81 | 0.273
2025-10-12 18:00 | 1760306400 | 1 | 0.0028 | 0.011 | 74.86 | 67.77 | 0.012
2025-10-12 19:00 | 1760310000 | 1 | 0 | 0 |  |  | 0
2025-10-12 20:00 | 1760313600 | 1 | 0 | 0 |  |  | 0
2025-10-12 21:00 | 1760317200 | 1 | 0 | 0 |  |  | 0
2025-10-12 22:00 | 1760320800 | 1 | 0.0833 | 0.312 | 73.11 | 65.51 | 0.347
2025-10-12 23:00 | 1760324400 | 1 | 0.0694 | 0.258 | 73.2 | 66.09 | 0.269
2025-10-13 00:00 | 1760328000 | 1 | 0.1028 | 0.384 | 73.74 | 68.88 | 0.273
2025-10-13 01:00 | 1760331600 | 1 | 0.3806 | 1.412 | 70.58 | 68.45 | 0.442
2025-10-13 02:00 | 1760335200 | 1 | 0.7861 | 2.941 | 68.46 | 67.29 | 0.505
2025-10-13 03:00 | 1760338800 | 1 | 1 | 3.924 | 67.42 | 66.35 | 0.618
2025-10-13 04:00 | 1760342400 | 1 | 1 | 4.187 | 66.32 | 65.32 | 0.619
2025-10-13 05:00 | 1760346000 | 1 | 1 | 4.707 | 65.34 | 64.43 | 0.63
2025-10-13 06:00 | 1760349600 | 1 | 1 | 5.446 | 64.49 | 63.75 | 0.592
2025-10-13 07:00 | 1760353200 | 1 | 1 | 5.506 | 63.58 | 62.88 | 0.568
2025-10-13 08:00 | 1760356800 | 1 | 1 | 5.49 | 62.99 | 62.3 | 0.553
2025-10-13 09:00 | 1760360400 | 1 | 1 | 3.162 | 62.44 | 61.7 | 0.344
2025-10-13 10:00 | 1760364000 | 1 | 1 | 3.163 | 61.96 | 61.29 | 0.309
2025-10-13 11:00 | 1760367600 | 1 | 1 | 3.161 | 61.55 | 60.93 | 0.286
2025-10-13 12:00 | 1760371200 | 1 | 1 | 3.159 | 61.24 | 60.66 | 0.27
2025-10-13 13:00 | 1760374800 | 1 | 1 | 3.01 | 60.99 | 60.44 | 0.243
2025-10-13 14:00 | 1760378400 | 1 | 1 | 2.186 | 60.79 | 60.26 | 0.168
2025-10-13 15:00 | 1760382000 | 1 | 1 | 2.036 | 60.64 | 60.13 | 0.152
2025-10-13 16:00 | 1760385600 | 1 | 1 | 2.035 | 60.46 | 59.95 | 0.154
2025-10-13 17:00 | 1760389200 | 1 | 1 | 2.034 | 60.32 | 59.84 | 0.144
2025-10-13 18:00 | 1760392800 | 1 | 1 | 2.036 | 60.21 | 59.74 | 0.142
2025-10-13 19:00 | 1760396400 | 1 | 1 | 2.079 | 60.1 | 59.61 | 0.147
2025-10-13 20:00 | 1760400000 | 1 | 1 | 2.033 | 60 | 59.54 | 0.139
2025-10-13 21:00 | 1760403600 | 1 | 1 | 2.124 | 59.88 | 59.44 | 0.138
2025-10-13 23:00 | 1760410800 | 1 | 1 | 2.271 | 59.65 | 59.17 | 0.162
2025-10-14 00:00 | 1760414400 | 1 | 1 | 2.754 | 59.49 | 59 | 0.196
2025-10-14 01:00 | 1760418000 | 1 | 1 | 3.036 | 59.31 | 58.82 | 0.216
2025-10-14 02:00 | 1760421600 | 1 | 0.8833 | 2.467 | 59.2 | 58.74 | 0.166
2025-10-14 03:00 | 1760425200 | 1 | 0 | 0 |  |  | 0
2025-10-14 04:00 | 1760428800 | 1 | 0 | 0 |  |  | 0
2025-10-14 05:00 | 1760432400 | 1 | 0 | 0 |  |  | 0
2025-10-14 06:00 | 1760436000 | 1 | 0 | 0 |  |  | 0
2025-10-14 07:00 | 1760439600 | 1 | 0 | 0 |  |  | 0
2025-10-14 08:00 | 1760443200 | 1 | 0 | 0 |  |  | 0
2025-10-14 09:00 | 1760446800 | 1 | 0 | 0 |  |  | 0
2025-10-14 10:00 | 1760450400 | 1 | 0 | 0 |  |  | 0
2025-10-14 11:00 | 1760454000 | 1 | 0 | 0 |  |  | 0
2025-10-14 12:00 | 1760457600 | 1 | 0 | 0 |  |  | 0
2025-10-14 13:00 | 1760461200 | 1 | 0 | 0 |  |  | 0
2025-10-14 14:00 | 1760464800 | 1 | 0 | 0 |  |  | 0
2025-10-14 15:00 | 1760468400 | 1 | 0.0028 | 0.005 | 57.43 | 56.71 | 0.001
2025-10-14 16:00 | 1760472000 | 1 | 0 | 0 |  |  | 0
2025-10-14 17:00 | 1760475600 | 1 | 0.025 | 0.05 | 58.41 | 58.04 | 0.002
2025-10-14 18:00 | 1760479200 | 1 | 0.0806 | 0.164 | 58.8 | 59.1 | -0.007
2025-10-14 19:00 | 1760482800 | 1 | 0 | 0 |  |  | 0
2025-10-14 20:00 | 1760486400 | 1 | 0 | 0 |  |  | 0
2025-10-14 21:00 | 1760490000 | 1 | 0 | 0 |  |  | 0
2025-10-14 22:00 | 1760493600 | 1 | 0 | 0 |  |  | 0
2025-10-14 23:00 | 1760497200 | 1 | 0 | 0 |  |  | 0
2025-10-15 00:00 | 1760500800 | 0.9972 | 0 | 0 |  |  | 0
2025-10-15 01:00 | 1760504400 | 1 | 0 | 0 |  |  | 0
2025-10-15 02:00 | 1760508000 | 1 | 0 | 0 |  |  | 0
2025-10-15 03:00 | 1760511600 | 1 | 0 | 0 |  |  | 0
2025-10-15 04:00 | 1760515200 | 1 | 0 | 0 |  |  | 0
2025-10-15 05:00 | 1760518800 | 1 | 0 | 0 |  |  | 0
2025-10-15 06:00 | 1760522400 | 1 | 0 | 0 |  |  | 0
2025-10-15 07:00 | 1760526000 | 1 | 0 | 0 |  |  | 0
2025-10-15 08:00 | 1760529600 | 1 | 0 | 0 |  |  | 0
2025-10-15 09:00 | 1760533200 | 1 | 0 | 0 |  |  | 0
2025-10-15 10:00 | 1760536800 | 1 | 0 | 0 |  |  | 0
2025-10-15 11:00 | 1760540400 | 1 | 0 | 0 |  |  | 0
2025-10-15 12:00 | 1760544000 | 1 | 0 | 0 |  |  | 0
2025-10-15 13:00 | 1760547600 | 1 | 0 | 0 |  |  | 0
2025-10-15 14:00 | 1760551200 | 1 | 0 | 0 |  |  | 0
2025-10-15 15:00 | 1760554800 | 1 | 0 | 0 |  |  | 0
2025-10-15 16:00 | 1760558400 | 1 | 0 | 0 |  |  | 0
2025-10-15 17:00 | 1760562000 | 1 | 0 | 0 |  |  | 0
2025-10-15 18:00 | 1760565600 | 1 | 0 | 0 |  |  | 0
2025-10-15 19:00 | 1760569200 | 1 | 0 | 0 |  |  | 0
2025-10-15 20:00 | 1760572800 | 1 | 0 | 0 |  |  | 0
2025-10-15 21:00 | 1760576400 | 1 | 0 | 0 |  |  | 0
2025-10-15 22:00 | 1760580000 | 1 | 0 | 0 |  |  | 0
2025-10-15 23:00 | 1760583600 | 1 | 0 | 0 |  |  | 0
2025-10-16 00:00 | 1760587200 | 1 | 0 | 0 |  |  | 0
2025-10-16 01:00 | 1760590800 | 1 | 0 | 0 |  |  | 0
2025-10-16 02:00 | 1760594400 | 1 | 0 | 0 |  |  | 0
2025-10-16 03:00 | 1760598000 | 1 | 0 | 0 |  |  | 0
2025-10-16 04:00 | 1760601600 | 1 | 0 | 0 |  |  | 0
2025-10-16 05:00 | 1760605200 | 1 | 0 | 0 |  |  | 0
2025-10-16 06:00 | 1760608800 | 1 | 0 | 0 |  |  | 0
2025-10-16 07:00 | 1760612400 | 1 | 0 | 0 |  |  | 0
2025-10-16 08:00 | 1760616000 | 1 | 0 | 0 |  |  | 0
2025-10-16 09:00 | 1760619600 | 1 | 0 | 0 |  |  | 0
2025-10-16 10:00 | 1760623200 | 1 | 0 | 0 |  |  | 0
2025-10-16 11:00 | 1760626800 | 1 | 0 | 0 |  |  | 0
2025-10-16 12:00 | 1760630400 | 1 | 0 | 0 |  |  | 0
2025-10-16 13:00 | 1760634000 | 1 | 0 | 0 |  |  | 0
2025-10-16 14:00 | 1760637600 | 1 | 0 | 0 |  |  | 0
2025-10-16 15:00 | 1760641200 | 1 | 0 | 0 |  |  | 0
2025-10-16 16:00 | 1760644800 | 1 | 0 | 0.001 |  |  | 0.002
2025-10-16 17:00 | 1760648400 | 1 | 0.2306 | 0.422 | 167.02 | 97.97 | 4.265
2025-10-16 18:00 | 1760652000 | 1 | 0 | 0 |  |  | 0
2025-10-16 19:00 | 1760655600 | 1 | 0.0833 | 0.173 | 160 | 80.1 | 2.027
2025-10-16 20:00 | 1760659200 | 1 | 0.1194 | 0.223 | 160.06 | 89.12 | 2.323
2025-10-16 21:00 | 1760662800 | 1 | 0.1 | 0.2 | 162.64 | 96.42 | 1.94
2025-10-16 22:00 | 1760666400 | 1 | 0.2694 | 0.502 | 126.63 | 89.95 | 2.698
2025-10-16 23:00 | 1760670000 | 1 | 0.2222 | 0.447 | 122.27 | 94.37 | 1.828
2025-10-17 00:00 | 1760673600 | 1 | 0.2306 | 0.543 | 131.08 | 93.08 | 3.013
2025-10-17 01:00 | 1760677200 | 1 | 0.2 | 0.403 | 137.33 | 96.09 | 2.433
2025-10-17 02:00 | 1760680800 | 1 | 0.1639 | 0.3 | 136.31 | 91.55 | 1.969
2025-10-17 03:00 | 1760684400 | 1 | 0.1889 | 0.381 | 140.89 | 94.07 | 2.614
2025-10-17 04:00 | 1760688000 | 1 | 0.175 | 0.305 | 141.72 | 91.95 | 2.226
2025-10-17 05:00 | 1760691600 | 1 | 0.0889 | 0.179 | 135.93 | 91.7 | 1.159
2025-10-17 06:00 | 1760695200 | 1 | 0.1194 | 0.232 | 154.76 | 93.21 | 2.082
2025-10-17 07:00 | 1760698800 | 0.9528 | 0.3586 | 0.673 | 145.82 | 82.74 | 5.929
2025-10-17 08:00 | 1760702400 | 1 | 0.0944 | 0.194 | 144.4 | 91.24 | 1.498
2025-10-17 09:00 | 1760706000 | 1 | 0.0889 | 0.179 | 143 | 89.09 | 1.411
2025-10-17 10:00 | 1760709600 | 1 | 0.0472 | 0.075 | 138.12 | 75.31 | 0.684
2025-10-17 11:00 | 1760713200 | 1 | 0 | 0 |  |  | 0
2025-10-17 12:00 | 1760716800 | 1 | 0 | 0 |  |  | 0
2025-10-17 13:00 | 1760720400 | 1 | 0 | 0 |  |  | 0
2025-10-17 14:00 | 1760724000 | 1 | 0.0278 | 0.056 | 118.34 | 63.78 | 0.446
2025-10-17 15:00 | 1760727600 | 1 | 0 | 0 |  |  | 0
2025-10-17 16:00 | 1760731200 | 1 | 0.0778 | 0.155 | 129.91 | 73.8 | 1.275
2025-10-17 17:00 | 1760734800 | 1 | 0 | 0 |  |  | 0
2025-10-17 18:00 | 1760738400 | 1 | 0.0778 | 0.156 | 125.91 | 74.47 | 1.179
2025-10-17 19:00 | 1760742000 | 1 | 0.0889 | 0.177 | 124.67 | 79.89 | 1.16
2025-10-17 20:00 | 1760745600 | 1 | 0.0833 | 0.172 | 118.02 | 80.69 | 0.932
2025-10-17 21:00 | 1760749200 | 1 | 0.0972 | 0.192 | 141.94 | 84.49 | 1.613
2025-10-17 22:00 | 1760752800 | 1 | 0.1639 | 0.294 | 141.89 | 86.56 | 2.369
2025-10-17 23:00 | 1760756400 | 1 | 0.0889 | 0.18 | 138.59 | 86.42 | 1.373
2025-10-18 00:00 | 1760760000 | 1 | 0.0889 | 0.178 | 136.97 | 87.1 | 1.301
2025-10-18 01:00 | 1760763600 | 1 | 0.1472 | 0.282 | 139.24 | 85.22 | 2.23
2025-10-18 02:00 | 1760767200 | 1 | 0.2306 | 0.426 | 141.27 | 90.25 | 3.182
2025-10-18 03:00 | 1760770800 | 1 | 0.0889 | 0.178 | 136.45 | 88.27 | 1.254
2025-10-18 04:00 | 1760774400 | 1 | 0.125 | 0.237 | 129.19 | 86.29 | 1.483
2025-10-18 05:00 | 1760778000 | 1 | 0.1972 | 0.359 | 150.93 | 91.67 | 3.113
2025-10-18 06:00 | 1760781600 | 1 | 0.1556 | 0.313 | 159.9 | 96.82 | 2.888
2025-10-18 07:00 | 1760785200 | 1 | 0.0833 | 0.168 | 143.05 | 87.14 | 1.377
2025-10-18 08:00 | 1760788800 | 1 | 0.1694 | 0.297 | 145.24 | 90.33 | 2.391
2025-10-18 09:00 | 1760792400 | 1 | 0.0833 | 0.167 | 141 | 83.93 | 1.394
2025-10-18 10:00 | 1760796000 | 1 | 0.0417 | 0.063 | 131.8 | 69.97 | 0.574
2025-10-18 11:00 | 1760799600 | 1 | 0.0111 | 0.015 | 143.9 | 85.49 | 0.13
2025-10-18 12:00 | 1760803200 | 1 | 0 | 0 |  |  | 0
2025-10-18 13:00 | 1760806800 | 1 | 0 | 0 |  |  | 0
2025-10-18 14:00 | 1760810400 | 1 | 0 | 0 |  |  | 0
2025-10-18 15:00 | 1760814000 | 1 | 0 | 0 |  |  | 0
2025-10-18 16:00 | 1760817600 | 1 | 0 | 0 |  |  | 0
2025-10-18 17:00 | 1760821200 | 1 | 0 | 0 |  |  | 0
2025-10-18 18:00 | 1760824800 | 1 | 0 | 0 |  |  | 0
2025-10-18 19:00 | 1760828400 | 1 | 0 | 0 |  |  | 0
2025-10-18 20:00 | 1760832000 | 1 | 0 | 0 |  |  | 0
2025-10-18 21:00 | 1760835600 | 1 | 0 | 0 |  |  | 0
2025-10-18 22:00 | 1760839200 | 1 | 0.0194 | 0.028 | 101.83 | 60.88 | 0.165
2025-10-18 23:00 | 1760842800 | 1 | 0.0861 | 0.125 | 123.15 | 78.75 | 0.814
2025-10-19 00:00 | 1760846400 | 1 | 0 | 0 |  |  | 0
2025-10-19 01:00 | 1760850000 | 1 | 0.0778 | 0.121 | 134.89 | 79.84 | 0.963
2025-10-19 02:00 | 1760853600 | 1 | 0 | 0 |  |  | 0
2025-10-19 03:00 | 1760857200 | 1 | 0.0806 | 0.127 | 132.65 | 80.19 | 0.963
2025-10-19 04:00 | 1760860800 | 0.95 | 0 | 0 |  |  | 0
2025-10-19 05:00 | 1760864400 | 1 | 0.0806 | 0.126 | 137.48 | 81.86 | 1.02
2025-10-19 06:00 | 1760868000 | 1 | 0 | 0 |  |  | 0
2025-10-19 07:00 | 1760871600 | 1 | 0.0806 | 0.119 | 152.85 | 84.44 | 1.197
2025-10-19 08:00 | 1760875200 | 1 | 0.0333 | 0.067 | 145.5 | 68.09 | 0.764
2025-10-19 09:00 | 1760878800 | 1 | 0.1583 | 0.276 | 155.39 | 81.83 | 2.979
2025-10-19 10:00 | 1760882400 | 1 | 0 | 0 |  |  | 0
2025-10-19 11:00 | 1760886000 | 1 | 0.2444 | 0.49 | 156.91 | 113.23 | 3.134
2025-10-19 12:00 | 1760889600 | 1 | 0.2944 | 0.588 | 157.44 | 130.26 | 2.34
2025-10-19 18:00 | 1760911200 | 1 | 0 | 0 |  |  | 0
2025-10-19 19:00 | 1760914800 | 1 | 0.0778 | 0.159 | 86.48 | 72.52 | 0.325
2025-10-19 20:00 | 1760918400 | 1 | 0.1194 | 0.22 | 119.44 | 74.24 | 1.459
2025-10-19 21:00 | 1760922000 | 1 | 0 | 0 |  |  | 0
2025-10-19 22:00 | 1760925600 | 1 | 0.0972 | 0.188 | 117.41 | 72.44 | 1.241
2025-10-19 23:00 | 1760929200 | 1 | 0.0639 | 0.098 | 123.01 | 82.65 | 0.575
2025-10-20 00:00 | 1760932800 | 1 | 0.0417 | 0.083 | 110.14 | 66.47 | 0.533
2025-10-20 01:00 | 1760936400 | 1 | 0.1139 | 0.191 | 126.45 | 78.81 | 1.329
2025-10-20 02:00 | 1760940000 | 1 | 0.0833 | 0.168 | 131.45 | 81.24 | 1.238
2025-10-20 03:00 | 1760943600 | 1 | 0.0778 | 0.157 | 125.83 | 78.12 | 1.098
2025-10-20 04:00 | 1760947200 | 1 | 0.1611 | 0.288 | 127.47 | 80.95 | 1.966
2025-10-20 05:00 | 1760950800 | 1 | 0 | 0 |  |  | 0
2025-10-20 06:00 | 1760954400 | 1 | 0.0833 | 0.168 | 133.51 | 80.81 | 1.296
2025-10-20 07:00 | 1760958000 | 1 | 0.1583 | 0.281 | 126.54 | 79.49 | 1.93
2025-10-20 08:00 | 1760961600 | 1 | 0 | 0 |  |  | 0
2025-10-20 09:00 | 1760965200 | 1 | 0.1556 | 0.275 | 125.16 | 78.39 | 1.879
2025-10-20 10:00 | 1760968800 | 1 | 0 | 0 |  |  | 0
2025-10-20 11:00 | 1760972400 | 1 | 0 | 0 |  |  | 0
2025-10-20 12:00 | 1760976000 | 1 | 0 | 0 |  |  | 0
2025-10-20 13:00 | 1760979600 | 1 | 0 | 0 |  |  | 0
2025-10-20 14:00 | 1760983200 | 1 | 0 | 0 |  |  | 0
2025-10-20 15:00 | 1760986800 | 1 | 0 | 0 |  |  | 0
2025-10-20 16:00 | 1760990400 | 1 | 0 | 0 |  |  | 0
2025-10-20 17:00 | 1760994000 | 1 | 0.0583 | 0.117 | 113.06 | 65.81 | 0.812
2025-10-20 18:00 | 1760997600 | 1 | 0.1139 | 0.186 | 120.9 | 80.69 | 1.094
2025-10-20 19:00 | 1761001200 | 1 | 0 | 0 |  |  | 0
2025-10-20 20:00 | 1761004800 | 1 | 0.0778 | 0.157 | 114.12 | 71.77 | 0.975
2025-10-20 21:00 | 1761008400 | 1 | 0 | 0 |  |  | 0
2025-10-20 22:00 | 1761012000 | 1 | 0.075 | 0.114 | 110.26 | 74.33 | 0.602
2025-10-20 23:00 | 1761015600 | 1 | 0 | 0 |  |  | 0
2025-10-21 00:00 | 1761019200 | 1 | 0 | 0 |  |  | 0
2025-10-21 01:00 | 1761022800 | 1 | 0.0778 | 0.115 | 106.57 | 73.21 | 0.561
2025-10-21 02:00 | 1761026400 | 1 | 0.0167 | 0.034 | 94.25 | 66.88 | 0.135
2025-10-21 03:00 | 1761030000 | 1 | 0.1833 | 0.312 | 124.71 | 72.25 | 2.402
2025-10-21 04:00 | 1761033600 | 1 | 0 | 0 |  |  | 0
2025-10-21 05:00 | 1761037200 | 1 | 0.0778 | 0.113 | 111.5 | 74.9 | 0.605
2025-10-21 06:00 | 1761040800 | 1 | 0.0778 | 0.158 | 114.28 | 73.98 | 0.931
2025-10-21 07:00 | 1761044400 | 1 | 0 | 0 |  |  | 0
2025-10-21 08:00 | 1761048000 | 1 | 0.0806 | 0.119 | 108.88 | 75.31 | 0.584
2025-10-21 09:00 | 1761051600 | 1 | 0.0889 | 0.179 | 109.76 | 72.93 | 0.968
2025-10-21 10:00 | 1761055200 | 1 | 0.0778 | 0.119 | 109.84 | 76.2 | 0.579
2025-10-21 11:00 | 1761058800 | 1 | 0.0778 | 0.157 | 110.44 | 75.21 | 0.811
2025-10-21 12:00 | 1761062400 | 1 | 0 | 0 |  |  | 0
2025-10-21 13:00 | 1761066000 | 1 | 0 | 0 |  |  | 0
2025-10-21 14:00 | 1761069600 | 1 | 0 | 0 |  |  | 0
2025-10-21 15:00 | 1761073200 | 1 | 0 | 0 |  |  | 0
2025-10-21 16:00 | 1761076800 | 1 | 0 | 0 |  |  | 0
2025-10-21 17:00 | 1761080400 | 1 | 0 | 0 |  |  | 0
2025-10-21 18:00 | 1761084000 | 1 | 0 | 0 |  |  | 0
2025-10-21 19:00 | 1761087600 | 1 | 0.0833 | 0.127 | 149.22 | 83.04 | 1.233
2025-10-21 20:00 | 1761091200 | 1 | 0 | 0 |  |  | 0
2025-10-21 21:00 | 1761094800 | 1 | 0 | 0 |  |  | 0
2025-10-21 22:00 | 1761098400 | 1 | 0 | 0 |  |  | 0
2025-10-21 23:00 | 1761102000 | 1 | 0.1694 | 0.3 | 149.24 | 81.91 | 2.963
2025-10-22 00:00 | 1761105600 | 0.9972 | 0 | 0 |  |  | 0
2025-10-22 01:00 | 1761109200 | 1 | 0.0778 | 0.156 | 145.43 | 79.02 | 1.517
2025-10-22 02:00 | 1761112800 | 1 | 0.0778 | 0.117 | 142.77 | 81.84 | 1.039
2025-10-22 03:00 | 1761116400 | 1 | 0.0833 | 0.167 | 146.39 | 81.7 | 1.588
2025-10-22 04:00 | 1761120000 | 1 | 0 | 0 |  |  | 0
2025-10-22 05:00 | 1761123600 | 1 | 0.1472 | 0.259 | 131.03 | 78.15 | 2.003
2025-10-22 06:00 | 1761127200 | 1 | 0.0083 | 0.013 | 135.09 | 100.51 | 0.065
2025-10-22 07:00 | 1761130800 | 1 | 0.0833 | 0.174 | 121.38 | 78.02 | 1.098
2025-10-22 08:00 | 1761134400 | 1 | 0.1111 | 0.206 | 120.92 | 76.72 | 1.336
2025-10-22 09:00 | 1761138000 | 1 | 0.1611 | 0.284 | 120.76 | 79.59 | 1.716
2025-10-22 10:00 | 1761141600 | 1 | 0.0833 | 0.169 | 120.54 | 80.04 | 1.002
2025-10-22 11:00 | 1761145200 | 1 | 0.125 | 0.229 | 118.29 | 76.74 | 1.394
2025-10-22 12:00 | 1761148800 | 1 | 0.1139 | 0.215 | 106.53 | 80.1 | 0.832
2025-10-22 13:00 | 1761152400 | 1 | 0.0833 | 0.168 | 99.14 | 75.49 | 0.584
2025-10-22 14:00 | 1761156000 | 1 | 0.0778 | 0.116 | 107.28 | 76.47 | 0.522
2025-10-22 15:00 | 1761159600 | 1 | 0 | 0 |  |  | 0
2025-10-22 16:00 | 1761163200 | 1 | 0 | 0 |  |  | 0
2025-10-22 17:00 | 1761166800 | 1 | 0.0806 | 0.124 | 95.32 | 71.71 | 0.428
2025-10-22 18:00 | 1761170400 | 1 | 0.0167 | 0.034 | 85.61 | 64.68 | 0.103
2025-10-22 19:00 | 1761174000 | 1 | 0.0778 | 0.114 | 96.69 | 71.74 | 0.415
2025-10-22 20:00 | 1761177600 | 1 | 0.2556 | 0.479 | 106.51 | 74.67 | 2.236
2025-10-22 21:00 | 1761181200 | 1 | 0 | 0 |  |  | 0
2025-10-22 22:00 | 1761184800 | 1 | 0.0833 | 0.168 | 119.29 | 75.92 | 1.07
2025-10-22 23:00 | 1761188400 | 1 | 0.0778 | 0.119 | 119.8 | 79.11 | 0.696
2025-10-23 00:00 | 1761192000 | 1 | 0.0139 | 0.028 | 99.55 | 71.01 | 0.117
2025-10-23 01:00 | 1761195600 | 1 | 0.1528 | 0.268 | 121.73 | 78.62 | 1.694
2025-10-23 02:00 | 1761199200 | 1 | 0.0778 | 0.157 | 133.7 | 79.45 | 1.248
2025-10-23 03:00 | 1761202800 | 1 | 0.1639 | 0.291 | 133.18 | 82.83 | 2.148
2025-10-23 04:00 | 1761206400 | 1 | 0.0889 | 0.18 | 127.94 | 83.08 | 1.183
2025-10-23 05:00 | 1761210000 | 1 | 0.1694 | 0.302 | 129.55 | 85.6 | 1.942
2025-10-23 06:00 | 1761213600 | 1 | 0.1667 | 0.296 | 150.44 | 89.72 | 2.63
2025-10-23 07:00 | 1761217200 | 1 | 0.0833 | 0.168 | 138.88 | 84.19 | 1.343
2025-10-23 08:00 | 1761220800 | 1 | 0.0778 | 0.119 | 136.93 | 83.49 | 0.929
2025-10-23 09:00 | 1761224400 | 1 | 0.0833 | 0.166 | 141.56 | 86.53 | 1.341
2025-10-23 10:00 | 1761228000 | 1 | 0.0833 | 0.17 | 134.6 | 80.25 | 1.347
2025-10-23 11:00 | 1761231600 | 1 | 0.0778 | 0.116 | 137.38 | 84.44 | 0.902
2025-10-23 12:00 | 1761235200 | 1 | 0 | 0 |  |  | 0
2025-10-23 13:00 | 1761238800 | 1 | 0 | 0 |  |  | 0
2025-10-23 14:00 | 1761242400 | 1 | 0 | 0 |  |  | 0
2025-10-23 15:00 | 1761246000 | 1 | 0 | 0 |  |  | 0
2025-10-23 16:00 | 1761249600 | 1 | 0 | 0 |  |  | 0
2025-10-23 17:00 | 1761253200 | 1 | 0.0778 | 0.118 | 150.68 | 81.91 | 1.191
2025-10-23 18:00 | 1761256800 | 1 | 0.0167 | 0.034 | 129.85 | 73.02 | 0.281
2025-10-23 19:00 | 1761260400 | 1 | 0.0778 | 0.164 | 153.13 | 78.63 | 1.778
2025-10-23 20:00 | 1761264000 | 1 | 0.0778 | 0.117 | 148.53 | 83.15 | 1.12
2025-10-23 21:00 | 1761267600 | 1 | 0.5944 | 1.186 | 151.8 | 126.02 | 4.479
2025-10-23 22:00 | 1761271200 | 1 | 1 | 2.012 | 136.08 | 118.72 | 5.119
2025-10-23 23:00 | 1761274800 | 1 | 0.6028 | 1.208 | 145.17 | 125.2 | 3.534
2025-10-24 00:00 | 1761278400 | 1 | 0.5028 | 1.016 | 141.01 | 115 | 3.864
2025-10-24 01:00 | 1761282000 | 1 | 0.2056 | 0.413 | 162.7 | 111.9 | 3.076
2025-10-24 02:00 | 1761285600 | 1 | 0.0944 | 0.188 | 164.25 | 105.18 | 1.631
2025-10-24 03:00 | 1761289200 | 1 | 0.1972 | 0.469 | 163.84 | 98.48 | 4.489
2025-10-24 04:00 | 1761292800 | 1 | 0.2 | 0.407 | 153.83 | 103.29 | 3.002
2025-10-24 05:00 | 1761296400 | 1 | 0.1 | 0.202 | 163.77 | 105.98 | 1.71
2025-10-24 06:00 | 1761300000 | 1 | 0.2472 | 0.54 | 139.42 | 98.11 | 3.261
2025-10-24 07:00 | 1761303600 | 1 | 0.1944 | 0.398 | 159.7 | 106.9 | 3.064
2025-10-24 08:00 | 1761307200 | 1 | 0.1889 | 0.379 | 155.69 | 103.16 | 2.921
2025-10-24 09:00 | 1761310800 | 1 | 0.0889 | 0.179 | 152.92 | 99.89 | 1.392
2025-10-24 10:00 | 1761314400 | 1 | 0.0889 | 0.178 | 151.48 | 96.49 | 1.437
2025-10-24 11:00 | 1761318000 | 1 | 0 | 0 |  |  | 0
2025-10-24 12:00 | 1761321600 | 1 | 0 | 0 |  |  | 0
2025-10-24 13:00 | 1761325200 | 1 | 0.0833 | 0.167 | 119.74 | 76.68 | 1.057
2025-10-24 14:00 | 1761328800 | 1 | 0 | 0 |  |  | 0
2025-10-24 15:00 | 1761332400 | 1 | 0 | 0 |  |  | 0
2025-10-24 16:00 | 1761336000 | 1 | 0 | 0 |  |  | 0
2025-10-24 17:00 | 1761339600 | 1 | 0 | 0 |  |  | 0
2025-10-24 18:00 | 1761343200 | 1 | 0 | 0 |  |  | 0
2025-10-24 19:00 | 1761346800 | 1 | 0 | 0 |  |  | 0
2025-10-24 20:00 | 1761350400 | 1 | 0 | 0 |  |  | 0
2025-10-24 21:00 | 1761354000 | 1 | 0.075 | 0.113 | 145.89 | 78.85 | 1.109
2025-10-24 22:00 | 1761357600 | 1 | 0.0083 | 0.017 | 106.22 | 72.94 | 0.082
2025-10-24 23:00 | 1761361200 | 1 | 0.0917 | 0.189 | 150.74 | 81.01 | 1.928
2025-10-25 00:00 | 1761364800 | 1 | 0.1139 | 0.215 | 149.09 | 81.39 | 2.138
2025-10-25 01:00 | 1761368400 | 1 | 0 | 0 |  |  | 0
2025-10-25 02:00 | 1761372000 | 1 | 0.1583 | 0.284 | 167.38 | 89.67 | 3.239
2025-10-25 03:00 | 1761375600 | 1 | 0 | 0 |  |  | 0
2025-10-25 04:00 | 1761379200 | 1 | 0.0778 | 0.157 | 160.52 | 80.69 | 1.838
2025-10-25 05:00 | 1761382800 | 1 | 0.0778 | 0.124 | 151.77 | 86.38 | 1.179
2025-10-25 06:00 | 1761386400 | 1 | 0.0778 | 0.157 | 168.16 | 86.32 | 1.884
2025-10-25 07:00 | 1761390000 | 1 | 0.0778 | 0.156 | 164.43 | 86.19 | 1.792
2025-10-25 08:00 | 1761393600 | 1 | 0.1583 | 0.285 | 163.73 | 88.81 | 3.131
2025-10-25 09:00 | 1761397200 | 1 | 0 | 0 |  |  | 0
2025-10-25 10:00 | 1761400800 | 1 | 0.0806 | 0.162 | 158.28 | 84.44 | 1.755
2025-10-25 11:00 | 1761404400 | 1 | 0 | 0 |  |  | 0
2025-10-25 12:00 | 1761408000 | 1 | 0.0667 | 0.103 | 153.16 | 79.8 | 1.103
2025-10-25 13:00 | 1761411600 | 1 | 0 | 0 |  |  | 0
2025-10-25 14:00 | 1761415200 | 1 | 0.0333 | 0.067 | 149.72 | 68.23 | 0.8
2025-10-25 15:00 | 1761418800 | 1 | 0 | 0 |  |  | 0
2025-10-25 16:00 | 1761422400 | 1 | 0.0806 | 0.165 | 157.44 | 79.29 | 1.892
2025-10-25 17:00 | 1761426000 | 1 | 0.0611 | 0.091 | 153.35 | 77.66 | 1.013
2025-10-25 18:00 | 1761429600 | 1 | 0.0806 | 0.165 | 159.33 | 85.08 | 1.792
2025-10-25 19:00 | 1761433200 | 1 | 0.0806 | 0.166 | 152.72 | 82.98 | 1.693
2025-10-25 20:00 | 1761436800 | 1 | 0.0194 | 0.039 | 141.28 | 76.01 | 0.374
2025-10-25 21:00 | 1761440400 | 1 | 0.0806 | 0.218 | 137.69 | 82.78 | 1.754
2025-10-25 22:00 | 1761444000 | 1 | 0.0861 | 0.175 | 160.83 | 88.13 | 1.869
2025-10-25 23:00 | 1761447600 | 1 | 0.1389 | 0.25 | 162.49 | 85.5 | 2.818
2025-10-26 00:00 | 1761451200 | 1 | 0.0583 | 0.12 | 152.81 | 79.97 | 1.278
2025-10-26 01:00 | 1761454800 | 1 | 0.0222 | 0.045 | 165.38 | 98.67 | 0.437
2025-10-26 02:00 | 1761458400 | 1 | 0.1806 | 0.315 | 156.37 | 85.74 | 3.264
2025-10-26 03:00 | 1761462000 | 1 | 0.0806 | 0.164 | 144.22 | 86.3 | 1.389
2025-10-26 04:00 | 1761465600 | 1 | 0.0778 | 0.156 | 160.55 | 86.11 | 1.7
2025-10-26 05:00 | 1761469200 | 1 | 0.05 | 0.075 | 156.1 | 77.55 | 0.869
2025-10-26 06:00 | 1761472800 | 1 | 0.0778 | 0.156 | 160.41 | 85.63 | 1.713
2025-10-26 07:00 | 1761476400 | 1 | 0.1083 | 0.21 | 154.39 | 83.26 | 2.201
2025-10-26 08:00 | 1761480000 | 1 | 0.0806 | 0.162 | 155.17 | 84.74 | 1.671
2025-10-26 09:00 | 1761483600 | 1 | 0.1528 | 0.274 | 155.45 | 87.46 | 2.723
2025-10-26 10:00 | 1761487200 | 1 | 0 | 0 |  |  | 0
2025-10-26 11:00 | 1761490800 | 1 | 0.0861 | 0.178 | 149.15 | 86.26 | 1.637
2025-10-26 12:00 | 1761494400 | 1 | 0.1139 | 0.211 | 146.54 | 85.58 | 1.883
2025-10-26 13:00 | 1761498000 | 1 | 0.0861 | 0.174 | 114.81 | 78.84 | 0.917
2025-10-26 14:00 | 1761501600 | 1 | 0.1611 | 0.284 | 152.24 | 87.6 | 2.687
2025-10-26 15:00 | 1761505200 | 1 | 0 | 0 |  |  | 0
2025-10-26 16:00 | 1761508800 | 1 | 0.0806 | 0.163 | 159.5 | 81.04 | 1.871
2025-10-26 17:00 | 1761512400 | 1 | 0.1583 | 0.28 | 162.69 | 86.86 | 3.111
2025-10-26 18:00 | 1761516000 | 1 | 0 | 0 |  |  | 0
2025-10-26 19:00 | 1761519600 | 1 | 0.0861 | 0.175 | 159.08 | 86.36 | 1.869
2025-10-26 20:00 | 1761523200 | 1 | 0.1083 | 0.207 | 159.66 | 82.45 | 2.343
2025-10-26 21:00 | 1761526800 | 1 | 0.1583 | 0.284 | 156.76 | 86.94 | 2.89
2025-10-26 22:00 | 1761530400 | 1 | 0.0861 | 0.171 | 156.05 | 89.54 | 1.666
2025-10-26 23:00 | 1761534000 | 1 | 0 | 0 |  |  | 0
2025-10-27 00:00 | 1761537600 | 1 | 0.1139 | 0.214 | 145.4 | 80.1 | 2.049
2025-10-27 01:00 | 1761541200 | 1 | 0.1167 | 0.235 | 114.43 | 77.61 | 1.27
2025-10-27 02:00 | 1761544800 | 1 | 0.2222 | 0.416 | 144.02 | 92.12 | 3.142
2025-10-27 03:00 | 1761548400 | 1 | 0.0861 | 0.17 | 164.39 | 90.78 | 1.831
2025-10-27 04:00 | 1761552000 | 1 | 0.0917 | 0.152 | 160.24 | 88.11 | 1.61
2025-10-27 05:00 | 1761555600 | 1 | 0.0667 | 0.133 | 170.77 | 92.87 | 1.512
2025-10-27 06:00 | 1761559200 | 1 | 0.0806 | 0.162 | 160.1 | 86.42 | 1.747
2025-10-27 07:00 | 1761562800 | 1 | 0.1139 | 0.289 | 162.82 | 86.47 | 3.239
2025-10-27 08:00 | 1761566400 | 1 | 0.0806 | 0.16 | 157.08 | 87.68 | 1.628
2025-10-27 09:00 | 1761570000 | 1 | 0.0806 | 0.16 | 153.14 | 85.26 | 1.59
2025-10-27 10:00 | 1761573600 | 1 | 0.0389 | 0.057 | 151.67 | 74.26 | 0.647
2025-10-27 11:00 | 1761577200 | 1 | 0.0861 | 0.174 | 149.83 | 84.85 | 1.661
2025-10-27 12:00 | 1761580800 | 1 | 0.1 | 0.276 | 118.06 | 79.22 | 1.566
2025-10-27 13:00 | 1761584400 | 1 | 0.0889 | 0.176 | 153.48 | 88.87 | 1.662
2025-10-27 14:00 | 1761588000 | 1 | 0.1083 | 0.262 | 152.25 | 84.83 | 2.589
2025-10-27 15:00 | 1761591600 | 1 | 0 | 0 |  |  | 0
2025-10-27 16:00 | 1761595200 | 1 | 0.0806 | 0.161 | 141.75 | 78.19 | 1.495
2025-10-27 17:00 | 1761598800 | 1 | 0.0778 | 0.117 | 140.83 | 81.41 | 1.013
2025-10-27 18:00 | 1761602400 | 1 | 0.0778 | 0.159 | 142.79 | 80.43 | 1.452
2025-10-27 19:00 | 1761606000 | 1 | 0.0861 | 0.173 | 139.4 | 83.56 | 1.416
2025-10-27 20:00 | 1761609600 | 1 | 0.1528 | 0.283 | 140.35 | 86.03 | 2.254
2025-10-27 21:00 | 1761613200 | 1 | 0.1278 | 0.254 | 127.47 | 85.07 | 1.578
2025-10-27 22:00 | 1761616800 | 1 | 0.2306 | 0.418 | 121.13 | 87.3 | 2.075
2025-10-27 23:00 | 1761620400 | 1 | 0.0972 | 0.196 | 142.09 | 91.02 | 1.466
2025-10-28 00:00 | 1761624000 | 1 | 0.1361 | 0.297 | 143.21 | 88.64 | 2.359
2025-10-28 01:00 | 1761627600 | 1 | 0.1833 | 0.373 | 116.55 | 83.75 | 1.793
2025-10-28 02:00 | 1761631200 | 1 | 0.175 | 0.313 | 160.63 | 95.24 | 2.995
2025-10-28 03:00 | 1761634800 | 1 | 0.0861 | 0.172 | 154.12 | 91.31 | 1.584
2025-10-28 04:00 | 1761638400 | 1 | 0.2472 | 0.462 | 151.43 | 90.3 | 4.131
2025-10-28 05:00 | 1761642000 | 1 | 0.0889 | 0.182 | 148.17 | 92.53 | 1.484
2025-10-28 06:00 | 1761645600 | 1 | 0.0944 | 0.274 | 164.32 | 91.28 | 2.929
2025-10-28 07:00 | 1761649200 | 1 | 0.0778 | 0.158 | 159.47 | 91.07 | 1.584
2025-10-28 08:00 | 1761652800 | 1 | 0.1528 | 0.271 | 159.58 | 88.83 | 2.803
2025-10-28 09:00 | 1761656400 | 1 | 0.0806 | 0.162 | 156.38 | 89.83 | 1.58
2025-10-28 10:00 | 1761660000 | 1 | 0 | 0 |  |  | 0
2025-10-28 11:00 | 1761663600 | 1 | 0.0667 | 0.103 | 146.71 | 79.71 | 1.012
2025-10-28 12:00 | 1761667200 | 1 | 0 | 0 |  |  | 0
2025-10-28 13:00 | 1761670800 | 1 | 0 | 0 |  |  | 0
2025-10-28 14:00 | 1761674400 | 1 | 0 | 0 |  |  | 0
2025-10-28 15:00 | 1761678000 | 1 | 0 | 0 |  |  | 0
2025-10-28 16:00 | 1761681600 | 1 | 0 | 0 |  |  | 0
2025-10-28 17:00 | 1761685200 | 1 | 0.0778 | 0.158 | 153.77 | 75.26 | 1.813
2025-10-28 18:00 | 1761688800 | 1 | 0.1111 | 0.209 | 157.71 | 80.22 | 2.37
2025-10-28 19:00 | 1761692400 | 1 | 0.0833 | 0.169 | 154.15 | 84.18 | 1.727
2025-10-28 20:00 | 1761696000 | 1 | 0.1611 | 0.287 | 156.86 | 89.42 | 2.821
2025-10-28 21:00 | 1761699600 | 1 | 0.0833 | 0.167 | 153.46 | 89.72 | 1.561
2025-10-28 22:00 | 1761703200 | 1 | 0.0861 | 0.262 | 123.89 | 83.51 | 1.549
2025-10-28 23:00 | 1761706800 | 1 | 0.1889 | 0.382 | 146.88 | 94.57 | 2.929
2025-10-29 00:00 | 1761710400 | 0.9861 | 0.169 | 0.3 | 161.08 | 95.2 | 2.855
2025-10-29 01:00 | 1761714000 | 1 | 0.0889 | 0.178 | 155 | 93.43 | 1.604
2025-10-29 02:00 | 1761717600 | 1 | 0.3083 | 0.786 | 129.22 | 91.51 | 4.343
2025-10-29 03:00 | 1761721200 | 1 | 0.1083 | 0.218 | 163.47 | 99.16 | 2.056
2025-10-29 04:00 | 1761724800 | 1 | 0.1667 | 0.303 | 161.37 | 95.65 | 2.909
2025-10-29 05:00 | 1761728400 | 1 | 0.1917 | 0.383 | 161.04 | 99.93 | 3.424
2025-10-29 06:00 | 1761732000 | 1 | 0.2417 | 0.503 | 136.38 | 94.64 | 3.073
2025-10-29 07:00 | 1761735600 | 1 | 0.2528 | 0.536 | 146.43 | 98.39 | 3.76
2025-10-29 08:00 | 1761739200 | 1 | 0.1917 | 0.385 | 144.26 | 100.38 | 2.476
2025-10-29 09:00 | 1761742800 | 1 | 0.2083 | 0.397 | 145.22 | 101.21 | 2.551
2025-10-29 10:00 | 1761746400 | 1 | 0.1889 | 0.376 | 137.92 | 96.57 | 2.277
2025-10-29 11:00 | 1761750000 | 1 | 0.1667 | 0.297 | 113.76 | 83.48 | 1.32
2025-10-29 12:00 | 1761753600 | 1 | 0.2333 | 0.505 | 116.2 | 83.93 | 2.386
2025-10-29 13:00 | 1761757200 | 1 | 0 | 0 |  |  | 0
2025-10-29 14:00 | 1761760800 | 1 | 0 | 0 |  |  | 0
2025-10-29 15:00 | 1761764400 | 1 | 0.0778 | 0.158 | 155.22 | 78.71 | 1.775
2025-10-29 16:00 | 1761768000 | 1 | 0 | 0 |  |  | 0
2025-10-29 17:00 | 1761771600 | 1 | 0.1556 | 0.278 | 157.67 | 84 | 3
2025-10-29 18:00 | 1761775200 | 1 | 0 | 0 |  |  | 0
2025-10-29 19:00 | 1761778800 | 1 | 0 | 0 |  |  | 0
2025-10-29 20:00 | 1761782400 | 1 | 0.025 | 0.037 | 128.2 | 66.3 | 0.333
2025-10-29 21:00 | 1761786000 | 1 | 0.0806 | 0.119 | 154.01 | 87.39 | 1.158
2025-10-29 22:00 | 1761789600 | 1 | 0.0222 | 0.034 | 123.74 | 68.82 | 0.27
2025-10-29 23:00 | 1761793200 | 1 | 0.0583 | 0.09 | 145.16 | 88.51 | 0.745
2025-10-30 00:00 | 1761796800 | 1 | 0.1583 | 0.278 | 163.25 | 84.61 | 3.208
2025-10-30 01:00 | 1761800400 | 1 | 0 | 0 |  |  | 0
2025-10-30 02:00 | 1761804000 | 1 | 0.1556 | 0.277 | 159.48 | 85.96 | 2.982
2025-10-30 03:00 | 1761807600 | 1 | 0.1639 | 0.294 | 155.18 | 87.13 | 2.928
2025-10-30 04:00 | 1761811200 | 1 | 0.0833 | 0.169 | 153.26 | 84.11 | 1.713
2025-10-30 05:00 | 1761814800 | 1 | 0.1667 | 0.295 | 125.1 | 83.08 | 1.815
2025-10-30 06:00 | 1761818400 | 1 | 0.1667 | 0.292 | 148.07 | 90.8 | 2.45
2025-10-30 07:00 | 1761822000 | 1 | 0.1361 | 0.28 | 166.58 | 90.34 | 3.133
2025-10-30 08:00 | 1761825600 | 1 | 0.0667 | 0.135 | 160.41 | 83.46 | 1.526
2025-10-30 09:00 | 1761829200 | 1 | 0.0944 | 0.156 | 161.88 | 93.24 | 1.556
2025-10-30 10:00 | 1761832800 | 1 | 0.0833 | 0.166 | 159.2 | 86.41 | 1.769
2025-10-30 11:00 | 1761836400 | 1 | 0.0806 | 0.121 | 152.52 | 86.27 | 1.172
2025-10-30 12:00 | 1761840000 | 1 | 0.0778 | 0.156 | 155.16 | 82.69 | 1.66
2025-10-30 13:00 | 1761843600 | 1 | 0.0778 | 0.12 | 147.72 | 83.35 | 1.133
2025-10-30 14:00 | 1761847200 | 1 | 0.0806 | 0.162 | 136.69 | 80.05 | 1.348
2025-10-30 15:00 | 1761850800 | 1 | 0 | 0 |  |  | 0
2025-10-30 16:00 | 1761854400 | 1 | 0.075 | 0.114 | 152.03 | 82.49 | 1.161
2025-10-30 17:00 | 1761858000 | 1 | 0.0444 | 0.089 | 148.13 | 69.33 | 1.026
2025-10-30 18:00 | 1761861600 | 1 | 0 | 0 |  |  | 0
2025-10-30 19:00 | 1761865200 | 1 | 0.1639 | 0.289 | 152.53 | 82.45 | 2.966
2025-10-30 20:00 | 1761868800 | 1 | 0 | 0 |  |  | 0
2025-10-30 21:00 | 1761872400 | 1 | 0.1583 | 0.281 | 151 | 83.13 | 2.795
2025-10-30 23:00 | 1761879600 | 1 | 0.0778 | 0.12 | 143.67 | 82.36 | 1.067
2025-10-31 00:00 | 1761883200 | 1 | 0 | 0 |  |  | 0
2025-10-31 01:00 | 1761886800 | 1 | 0.0806 | 0.163 | 141.82 | 76.83 | 1.549
2025-10-31 02:00 | 1761890400 | 1 | 0.0778 | 0.115 | 141.08 | 82.67 | 0.988
2025-10-31 03:00 | 1761894000 | 1 | 0.0778 | 0.156 | 135.86 | 76.14 | 1.363
2025-10-31 04:00 | 1761897600 | 1 | 0.0778 | 0.118 | 134.38 | 82.6 | 0.89
2025-10-31 05:00 | 1761901200 | 1 | 0 | 0 |  |  | 0
2025-10-31 06:00 | 1761904800 | 1 | 0.0806 | 0.122 | 110.89 | 76.35 | 0.616
2025-10-31 07:00 | 1761908400 | 1 | 0.1556 | 0.274 | 144.07 | 80.44 | 2.555
2025-10-31 08:00 | 1761912000 | 1 | 0 | 0 |  |  | 0
2025-10-31 09:00 | 1761915600 | 1 | 0 | 0 |  |  | 0
2025-10-31 10:00 | 1761919200 | 1 | 0.0778 | 0.116 | 136.64 | 80.65 | 0.955
2025-10-31 11:00 | 1761922800 | 1 | 0.0083 | 0.017 | 108.37 | 77.19 | 0.077
2025-10-31 12:00 | 1761926400 | 1 | 0.0806 | 0.121 | 133.71 | 79.54 | 0.958
2025-10-31 13:00 | 1761930000 | 1 | 0 | 0 |  |  | 0
2025-10-31 14:00 | 1761933600 | 1 | 0 | 0 |  |  | 0
2025-10-31 15:00 | 1761937200 | 1 | 0 | 0 |  |  | 0
2025-10-31 16:00 | 1761940800 | 1 | 0.0389 | 0.058 | 121.3 | 64.44 | 0.48
2025-10-31 17:00 | 1761944400 | 1 | 0 | 0 |  |  | 0
2025-10-31 18:00 | 1761948000 | 1 | 0 | 0 |  |  | 0
2025-10-31 19:00 | 1761951600 | 1 | 0.0778 | 0.114 | 125.91 | 76.39 | 0.823
2025-10-31 20:00 | 1761955200 | 1 | 0 | 0 |  |  | 0
2025-10-31 21:00 | 1761958800 | 1 | 0.0778 | 0.115 | 125.4 | 77.96 | 0.803
2025-10-31 22:00 | 1761962400 | 1 | 0 | 0 |  |  | 0
2025-10-31 23:00 | 1761966000 | 1 | 0.0778 | 0.118 | 148.78 | 82.48 | 1.15
2025-11-01 00:00 | 1761969600 | 1 | 0.0083 | 0.017 | 112.46 | 71.7 | 0.1
2025-11-01 01:00 | 1761973200 | 1 | 0.1417 | 0.246 | 151.01 | 79.2 | 2.58
2025-11-01 02:00 | 1761976800 | 1 | 0.0222 | 0.045 | 156.92 | 99.81 | 0.374
2025-11-01 03:00 | 1761980400 | 1 | 0.0833 | 0.125 | 146.74 | 85.67 | 1.117
2025-11-01 04:00 | 1761984000 | 1 | 0.0806 | 0.16 | 101.41 | 74.26 | 0.636
2025-11-01 05:00 | 1761987600 | 1 | 0.1444 | 0.291 | 161.53 | 85.73 | 3.228
2025-11-01 06:00 | 1761991200 | 1 | 0 | 0 |  |  | 0
2025-11-01 07:00 | 1761994800 | 1 | 0.1611 | 0.283 | 157.87 | 85.02 | 3.018
2025-11-01 08:00 | 1761998400 | 1 | 0 | 0 |  |  | 0
2025-11-01 09:00 | 1762002000 | 1 | 0.15 | 0.284 | 155.37 | 84.21 | 2.945
2025-11-01 10:00 | 1762005600 | 1 | 0 | 0 |  |  | 0
2025-11-01 11:00 | 1762009200 | 1 | 0.1639 | 0.285 | 135.53 | 81.05 | 2.273
2025-11-01 12:00 | 1762012800 | 1 | 0 | 0 |  |  | 0
2025-11-01 13:00 | 1762016400 | 1 | 0.1639 | 0.294 | 118.64 | 76.96 | 1.788
2025-11-01 14:00 | 1762020000 | 1 | 0.0806 | 0.122 | 141.48 | 84.81 | 1.01
2025-11-01 15:00 | 1762023600 | 1 | 0.0861 | 0.171 | 153.12 | 86.16 | 1.677
2025-11-01 16:00 | 1762027200 | 1 | 0.1611 | 0.289 | 142.3 | 82.39 | 2.533
2025-11-01 17:00 | 1762030800 | 1 | 0 | 0 |  |  | 0
2025-11-01 18:00 | 1762034400 | 1 | 0.1722 | 0.305 | 141.61 | 85.62 | 2.502
2025-11-01 19:00 | 1762038000 | 1 | 0.1694 | 0.3 | 139.34 | 85.01 | 2.39
2025-11-01 20:00 | 1762041600 | 1 | 0.0861 | 0.172 | 131.91 | 84.94 | 1.182
2025-11-01 21:00 | 1762045200 | 1 | 0.1694 | 0.295 | 143.22 | 86.61 | 2.444
2025-11-01 22:00 | 1762048800 | 1 | 0.0861 | 0.132 | 135.35 | 83.86 | 0.996
2025-11-01 23:00 | 1762052400 | 1 | 0.0806 | 0.161 | 139.77 | 80.92 | 1.391
2025-11-02 00:00 | 1762056000 | 1 | 0.1722 | 0.297 | 137.69 | 84.4 | 2.321
2025-11-02 01:00 | 1762059600 | 1 | 0.175 | 0.308 | 147.12 | 88.28 | 2.657
2025-11-02 01:00 | 1762063200 | 1 | 0.1694 | 0.298 | 141.75 | 86.55 | 2.407
2025-11-02 02:00 | 1762066800 | 1 | 0.0861 | 0.172 | 140.38 | 86.72 | 1.348
2025-11-02 03:00 | 1762070400 | 1 | 0.2694 | 0.503 | 116.16 | 82.94 | 2.444
2025-11-02 04:00 | 1762074000 | 1 | 0.1806 | 0.322 | 146.1 | 93.04 | 2.503
2025-11-02 05:00 | 1762077600 | 1 | 0.2444 | 0.448 | 133.21 | 86.5 | 3.057
2025-11-02 06:00 | 1762081200 | 1 | 0.1722 | 0.353 | 141.69 | 91.88 | 2.574
2025-11-02 07:00 | 1762084800 | 1 | 0.0944 | 0.188 | 166.61 | 93.95 | 2.002
2025-11-02 08:00 | 1762088400 | 1 | 0.1667 | 0.296 | 168.83 | 93.91 | 3.253
2025-11-02 09:00 | 1762092000 | 1 | 0.0806 | 0.124 | 162.05 | 89.32 | 1.325
2025-11-02 10:00 | 1762095600 | 1 | 0 | 0 |  |  | 0
2025-11-02 11:00 | 1762099200 | 1 | 0.025 | 0.038 | 134.31 | 67.88 | 0.37
2025-11-02 12:00 | 1762102800 | 1 | 0 | 0 |  |  | 0
2025-11-02 13:00 | 1762106400 | 1 | 0 | 0 |  |  | 0
2025-11-02 14:00 | 1762110000 | 1 | 0 | 0 |  |  | 0
2025-11-02 15:00 | 1762113600 | 1 | 0.1583 | 0.273 | 162.8 | 82.91 | 3.2
2025-11-02 16:00 | 1762117200 | 1 | 0.0806 | 0.161 | 158.22 | 82.88 | 1.773
2025-11-02 17:00 | 1762120800 | 1 | 0.1611 | 0.285 | 159.96 | 87.45 | 3.026
2025-11-02 18:00 | 1762124400 | 1 | 0 | 0 |  |  | 0
2025-11-02 19:00 | 1762128000 | 1 | 0.0861 | 0.169 | 165 | 84.4 | 1.995
2025-11-02 20:00 | 1762131600 | 1 | 0.1028 | 0.174 | 160.67 | 80.88 | 2.033
2025-11-02 21:00 | 1762135200 | 1 | 0.0444 | 0.086 | 170.95 | 91.17 | 1.002
2025-11-02 22:00 | 1762138800 | 1 | 0.1611 | 0.289 | 164.11 | 87.88 | 3.22
2025-11-02 23:00 | 1762142400 | 1 | 0.0861 | 0.17 | 158.4 | 84.32 | 1.844
2025-11-03 00:00 | 1762146000 | 1 | 0.0833 | 0.127 | 135.5 | 86.99 | 0.9
2025-11-03 01:00 | 1762149600 | 1 | 0.1611 | 0.287 | 162.82 | 87.84 | 3.155
2025-11-03 02:00 | 1762153200 | 1 | 0.0778 | 0.158 | 138.53 | 81.7 | 1.311
2025-11-03 03:00 | 1762156800 | 1 | 0.1611 | 0.286 | 167.52 | 90.05 | 3.24
2025-11-03 04:00 | 1762160400 | 1 | 0.0833 | 0.169 | 161.89 | 87.79 | 1.835
2025-11-03 05:00 | 1762164000 | 1 | 0.0861 | 0.136 | 148.28 | 89.91 | 1.165
2025-11-03 06:00 | 1762167600 | 1 | 0.1583 | 0.281 | 168.23 | 91.62 | 3.146
2025-11-03 07:00 | 1762171200 | 1 | 0.0861 | 0.172 | 168.71 | 92.56 | 1.914
2025-11-03 08:00 | 1762174800 | 1 | 0.1611 | 0.287 | 164.62 | 90.22 | 3.122
2025-11-03 09:00 | 1762178400 | 1 | 0.0861 | 0.169 | 160.09 | 85.44 | 1.844
2025-11-03 10:00 | 1762182000 | 1 | 0 | 0 |  |  | 0
2025-11-03 11:00 | 1762185600 | 1 | 0 | 0 |  |  | 0
2025-11-03 12:00 | 1762189200 | 1 | 0 | 0 |  |  | 0
2025-11-03 13:00 | 1762192800 | 1 | 0 | 0 |  |  | 0
2025-11-03 14:00 | 1762196400 | 1 | 0 | 0 |  |  | 0
2025-11-03 15:00 | 1762200000 | 1 | 0.1111 | 0.226 | 144.55 | 77.08 | 2.236
2025-11-03 16:00 | 1762203600 | 1 | 0 | 0 |  |  | 0
2025-11-03 17:00 | 1762207200 | 1 | 0.0778 | 0.157 | 144.17 | 78.89 | 1.498
2025-11-03 18:00 | 1762210800 | 1 | 0.0806 | 0.16 | 140.28 | 79.7 | 1.424
2025-11-03 19:00 | 1762214400 | 1 | 0 | 0 |  |  | 0
2025-11-03 20:00 | 1762218000 | 1 | 0.0806 | 0.16 | 131.63 | 76.82 | 1.281
2025-11-03 21:00 | 1762221600 | 1 | 0.0861 | 0.17 | 121.49 | 77.34 | 1.096
2025-11-03 22:00 | 1762225200 | 1 | 0.0833 | 0.168 | 110.28 | 76.91 | 0.818
2025-11-03 23:00 | 1762228800 | 1 | 0.0917 | 0.184 | 100.69 | 76.95 | 0.639
2025-11-04 00:00 | 1762232400 | 1 | 0 | 0 |  |  | 0
2025-11-04 01:00 | 1762236000 | 1 | 0.0778 | 0.155 | 138.8 | 76.17 | 1.422
2025-11-04 02:00 | 1762239600 | 1 | 0.0833 | 0.169 | 162.38 | 84.13 | 1.935
2025-11-04 03:00 | 1762243200 | 1 | 0.0806 | 0.157 | 159.58 | 83.35 | 1.755
2025-11-04 04:00 | 1762246800 | 1 | 0 | 0 |  |  | 0
2025-11-04 05:00 | 1762250400 | 1 | 0.0778 | 0.157 | 157.95 | 83.09 | 1.72
2025-11-04 06:00 | 1762254000 | 1 | 0.0833 | 0.166 | 156.57 | 85.14 | 1.74
2025-11-04 07:00 | 1762257600 | 1 | 0.0778 | 0.157 | 153.73 | 82.66 | 1.633
2025-11-04 08:00 | 1762261200 | 1 | 0.0861 | 0.167 | 153.36 | 84.52 | 1.689
2025-11-04 09:00 | 1762264800 | 1 | 0 | 0 |  |  | 0
2025-11-04 10:00 | 1762268400 | 1 | 0 | 0 |  |  | 0
2025-11-04 11:00 | 1762272000 | 1 | 0 | 0 |  |  | 0
2025-11-04 12:00 | 1762275600 | 1 | 0.0861 | 0.169 | 142.45 | 74.87 | 1.676
2025-11-04 13:00 | 1762279200 | 1 | 0 | 0 |  |  | 0
2025-11-04 14:00 | 1762282800 | 1 | 0.0806 | 0.158 | 145 | 81.05 | 1.48
2025-11-04 15:00 | 1762286400 | 1 | 0.0833 | 0.169 | 163.21 | 85.78 | 1.912
2025-11-04 16:00 | 1762290000 | 1 | 0.0833 | 0.168 | 162.75 | 88.92 | 1.819
2025-11-04 17:00 | 1762293600 | 1 | 0.0833 | 0.168 | 159.8 | 85.81 | 1.818
2025-11-04 18:00 | 1762297200 | 1 | 0.1056 | 0.213 | 160.74 | 92.88 | 2.117
2025-11-04 19:00 | 1762300800 | 1 | 0.1306 | 0.277 | 161.11 | 87.84 | 2.959
2025-11-04 20:00 | 1762304400 | 1 | 0.0778 | 0.157 | 154.36 | 82.6 | 1.65
2025-11-04 21:00 | 1762308000 | 1 | 0.0833 | 0.168 | 151.63 | 85.57 | 1.622
2025-11-04 22:00 | 1762311600 | 1 | 0.0833 | 0.169 | 147.52 | 86.02 | 1.522
2025-11-04 23:00 | 1762315200 | 1 | 0.0833 | 0.169 | 138.03 | 86.75 | 1.266
2025-11-05 00:00 | 1762318800 | 0.9972 | 0.156 | 0.284 | 153.87 | 87.28 | 2.744
2025-11-05 01:00 | 1762322400 | 1 | 0.0833 | 0.168 | 149.14 | 87.3 | 1.524
2025-11-05 02:00 | 1762326000 | 1 | 0.0889 | 0.181 | 163.98 | 90.9 | 1.933
2025-11-05 03:00 | 1762329600 | 1 | 0.0833 | 0.167 | 151.47 | 88.99 | 1.53
2025-11-05 04:00 | 1762333200 | 1 | 0.1222 | 0.226 | 163.88 | 84.87 | 2.61
2025-11-05 05:00 | 1762336800 | 1 | 0.0833 | 0.165 | 168.26 | 89.29 | 1.911
2025-11-05 06:00 | 1762340400 | 1 | 0.0833 | 0.168 | 137.81 | 87.25 | 1.245
2025-11-05 07:00 | 1762344000 | 1 | 0.1556 | 0.279 | 167.75 | 90.88 | 3.146
2025-11-05 08:00 | 1762347600 | 1 | 0 | 0 |  |  | 0
2025-11-05 09:00 | 1762351200 | 1 | 0.0833 | 0.171 | 159.78 | 85.58 | 1.848
2025-11-05 10:00 | 1762354800 | 1 | 0 | 0 |  |  | 0
2025-11-05 11:00 | 1762358400 | 1 | 0.0778 | 0.158 | 154.59 | 79.18 | 1.749
2025-11-05 12:00 | 1762362000 | 1 | 0.0417 | 0.084 | 150.12 | 72.29 | 0.956
2025-11-05 13:00 | 1762365600 | 1 | 0.0361 | 0.073 | 163.18 | 90.82 | 0.773
2025-11-05 14:00 | 1762369200 | 1 | 0 | 0 |  |  | 0
2025-11-05 15:00 | 1762372800 | 1 | 0.0778 | 0.157 | 158.84 | 79.05 | 1.831
2025-11-05 16:00 | 1762376400 | 1 | 0.0833 | 0.167 | 158.3 | 83.33 | 1.836
2025-11-05 17:00 | 1762380000 | 1 | 0 | 0 |  |  | 0
2025-11-05 18:00 | 1762383600 | 1 | 0.0778 | 0.156 | 155.69 | 82.53 | 1.669
2025-11-05 19:00 | 1762387200 | 1 | 0.0833 | 0.177 | 155.26 | 85.52 | 1.794
2025-11-05 20:00 | 1762390800 | 1 | 0.1444 | 0.263 | 153.13 | 81.46 | 2.753
2025-11-05 21:00 | 1762394400 | 1 | 0.0361 | 0.074 | 143.53 | 76.17 | 0.727
2025-11-05 22:00 | 1762398000 | 1 | 0.1056 | 0.213 | 150.72 | 86.22 | 2.01
2025-11-05 23:00 | 1762401600 | 1 | 0.1222 | 0.243 | 144.67 | 92.08 | 1.869
2025-11-06 00:00 | 1762405200 | 1 | 0.0889 | 0.246 | 161.21 | 83.88 | 2.787
2025-11-06 01:00 | 1762408800 | 1 | 0.0361 | 0.072 | 147.95 | 78.29 | 0.737
2025-11-06 02:00 | 1762412400 | 1 | 0.0472 | 0.095 | 163.28 | 94.3 | 0.964
2025-11-06 03:00 | 1762416000 | 1 | 0.1833 | 0.379 | 118.57 | 83.75 | 1.936
2025-11-06 04:00 | 1762419600 | 1 | 0.0889 | 0.18 | 160.79 | 94.44 | 1.741
2025-11-06 05:00 | 1762423200 | 1 | 0.1444 | 0.263 | 157.57 | 86.49 | 2.735
2025-11-06 06:00 | 1762426800 | 1 | 0.0917 | 0.185 | 130.74 | 88.33 | 1.15
2025-11-06 07:00 | 1762430400 | 1 | 0.15 | 0.304 | 158.48 | 88.32 | 3.125
2025-11-06 08:00 | 1762434000 | 1 | 0.0556 | 0.113 | 154.97 | 92.07 | 1.044
2025-11-06 09:00 | 1762437600 | 1 | 0.0944 | 0.191 | 156.56 | 86.12 | 1.969
2025-11-06 10:00 | 1762441200 | 1 | 0.0361 | 0.073 | 160.91 | 98.14 | 0.668
2025-11-06 11:00 | 1762444800 | 1 | 0.0833 | 0.167 | 111.58 | 77.13 | 0.842
2025-11-06 12:00 | 1762448400 | 1 | 0.0778 | 0.223 | 151.45 | 78.37 | 2.389
2025-11-06 13:00 | 1762452000 | 1 | 0.025 | 0.05 | 156.22 | 102.03 | 0.397
2025-11-06 14:00 | 1762455600 | 1 | 0.1833 | 0.371 | 117.45 | 83.53 | 1.846
2025-11-06 15:00 | 1762459200 | 1 | 0.0889 | 0.18 | 157.9 | 92.76 | 1.719
2025-11-06 16:00 | 1762462800 | 1 | 0.0833 | 0.169 | 155.83 | 90.19 | 1.622
2025-11-06 17:00 | 1762466400 | 1 | 0.0889 | 0.178 | 153.48 | 85.91 | 1.76
2025-11-06 18:00 | 1762470000 | 1 | 0.15 | 0.269 | 154 | 85.05 | 2.718
2025-11-06 19:00 | 1762473600 | 1 | 0.0944 | 0.189 | 151.27 | 89.81 | 1.703
2025-11-06 20:00 | 1762477200 | 1 | 0.1944 | 0.393 | 136.01 | 91.51 | 2.563
2025-11-06 21:00 | 1762480800 | 1 | 0.1611 | 0.291 | 160.91 | 93.1 | 2.888
2025-11-06 22:00 | 1762484400 | 1 | 0.1778 | 0.358 | 149.3 | 93.85 | 2.906
2025-11-06 23:00 | 1762488000 | 1 | 0.0889 | 0.179 | 160.35 | 94.42 | 1.726
2025-11-07 00:00 | 1762491600 | 1 | 0.1611 | 0.291 | 159.09 | 91.5 | 2.885
2025-11-07 01:00 | 1762495200 | 1 | 0.2 | 0.402 | 124.02 | 90.79 | 1.958
2025-11-07 02:00 | 1762498800 | 1 | 0.1889 | 0.382 | 166.67 | 99.54 | 3.747
2025-11-07 03:00 | 1762502400 | 1 | 0.0889 | 0.179 | 164.36 | 96.15 | 1.785
2025-11-07 04:00 | 1762506000 | 1 | 0.1556 | 0.279 | 144.03 | 89.84 | 2.213
2025-11-07 05:00 | 1762509600 | 1 | 0.1889 | 0.381 | 165.08 | 97.22 | 3.788
2025-11-07 06:00 | 1762513200 | 1 | 0.0944 | 0.188 | 170.88 | 98.98 | 1.984
2025-11-07 07:00 | 1762516800 | 1 | 0.1556 | 0.28 | 163.51 | 92.93 | 2.895
2025-11-07 08:00 | 1762520400 | 1 | 0.0889 | 0.178 | 160.34 | 94.91 | 1.711
2025-11-07 09:00 | 1762524000 | 1 | 0.1083 | 0.221 | 155.43 | 91.54 | 2.073
2025-11-07 10:00 | 1762527600 | 1 | 0.1583 | 0.398 | 159.82 | 89.15 | 4.119
2025-11-07 11:00 | 1762531200 | 1 | 0.0944 | 0.19 | 154.61 | 91.65 | 1.748
2025-11-07 12:00 | 1762534800 | 1 | 0.0944 | 0.192 | 151.71 | 92.12 | 1.657
2025-11-07 13:00 | 1762538400 | 1 | 0.0889 | 0.183 | 127.48 | 89.09 | 1.027
2025-11-07 14:00 | 1762542000 | 1 | 0.1778 | 0.358 | 145.1 | 92.03 | 2.785
2025-11-07 15:00 | 1762545600 | 1 | 0.0944 | 0.191 | 162.02 | 97.1 | 1.815
2025-11-07 16:00 | 1762549200 | 1 | 0.1389 | 0.276 | 164.2 | 91.17 | 2.933
2025-11-07 17:00 | 1762552800 | 1 | 0.0889 | 0.182 | 160.39 | 94.05 | 1.756
2025-11-07 18:00 | 1762556400 | 1 | 0.0833 | 0.167 | 158.41 | 90.87 | 1.658
2025-11-07 19:00 | 1762560000 | 1 | 0.1722 | 0.344 | 156.55 | 90.81 | 3.312
2025-11-07 20:00 | 1762563600 | 1 | 0.1306 | 0.291 | 111.27 | 80.58 | 1.308
2025-11-07 21:00 | 1762567200 | 1 | 0.1194 | 0.24 | 151.19 | 91.54 | 2.094
2025-11-07 22:00 | 1762570800 | 1 | 0.1639 | 0.333 | 137.24 | 95.1 | 2.051
2025-11-07 23:00 | 1762574400 | 1 | 0.1639 | 0.301 | 166.75 | 94.66 | 3.175
2025-11-08 00:00 | 1762578000 | 1 | 0.1833 | 0.373 | 147.36 | 95.41 | 2.808
2025-11-08 01:00 | 1762581600 | 1 | 0.0889 | 0.181 | 161.4 | 93.98 | 1.786
2025-11-08 02:00 | 1762585200 | 1 | 0.0889 | 0.177 | 159.01 | 90.93 | 1.766
2025-11-08 03:00 | 1762588800 | 1 | 0.2444 | 0.45 | 122.97 | 84.52 | 2.534
2025-11-08 04:00 | 1762592400 | 1 | 0.1083 | 0.222 | 149.11 | 96.85 | 1.681
2025-11-08 05:00 | 1762596000 | 1 | 0.1611 | 0.286 | 152.75 | 90.98 | 2.586
2025-11-08 06:00 | 1762599600 | 1 | 0.175 | 0.353 | 148.62 | 91.29 | 2.966
2025-11-08 07:00 | 1762603200 | 1 | 0.0167 | 0.038 | 126.43 | 82.78 | 0.243
2025-11-08 08:00 | 1762606800 | 1 | 0.0694 | 0.14 | 149.38 | 85.12 | 1.314
2025-11-08 09:00 | 1762610400 | 1 | 0.0917 | 0.267 | 143.92 | 80.63 | 2.477
2025-11-08 10:00 | 1762614000 | 1 | 0.0111 | 0.023 | 99.75 | 70.36 | 0.101
2025-11-08 11:00 | 1762617600 | 1 | 0.1083 | 0.217 | 134.91 | 76.26 | 1.867
2025-11-08 12:00 | 1762621200 | 1 | 0.0472 | 0.098 | 135.1 | 88.5 | 0.661
2025-11-08 13:00 | 1762624800 | 1 | 0 | 0 |  |  | 0
2025-11-08 14:00 | 1762628400 | 1 | 0.0222 | 0.044 | 105.68 | 66.02 | 0.256
2025-11-08 15:00 | 1762632000 | 1 | 0.0917 | 0.185 | 129 | 78.06 | 1.381
2025-11-08 16:00 | 1762635600 | 1 | 0.0833 | 0.168 | 127.17 | 82.17 | 1.107
2025-11-08 17:00 | 1762639200 | 1 | 0.0833 | 0.168 | 125.8 | 80.44 | 1.117
2025-11-08 18:00 | 1762642800 | 1 | 0.0833 | 0.168 | 125.3 | 81.43 | 1.081
2025-11-08 19:00 | 1762646400 | 1 | 0.1639 | 0.332 | 124.91 | 82.89 | 2.039
2025-11-08 20:00 | 1762650000 | 1 | 0.1028 | 0.209 | 125.34 | 87.79 | 1.149
2025-11-08 21:00 | 1762653600 | 1 | 0.0944 | 0.194 | 124.73 | 87.44 | 1.049
2025-11-08 22:00 | 1762657200 | 1 | 0.1889 | 0.423 | 121.76 | 84.52 | 2.308
2025-11-08 23:00 | 1762660800 | 1 | 0.2556 | 0.472 | 129.02 | 87.55 | 2.868
2025-11-09 00:00 | 1762664400 | 1 | 0.0917 | 0.185 | 148.34 | 93.08 | 1.495
2025-11-09 01:00 | 1762668000 | 1 | 0.0889 | 0.178 | 146.42 | 90.17 | 1.465
2025-11-09 02:00 | 1762671600 | 1 | 0.2083 | 0.466 | 146.58 | 89.17 | 3.919
2025-11-09 03:00 | 1762675200 | 1 | 0.0944 | 0.191 | 143.66 | 93.93 | 1.393
2025-11-09 04:00 | 1762678800 | 1 | 0.2667 | 0.497 | 141.68 | 92.76 | 3.554
2025-11-09 05:00 | 1762682400 | 1 | 0.1583 | 0.317 | 148.45 | 92.17 | 2.617
2025-11-09 06:00 | 1762686000 | 1 | 0.1194 | 0.239 | 162.42 | 101.73 | 2.124
2025-11-09 07:00 | 1762689600 | 1 | 0.1556 | 0.279 | 158.64 | 91.68 | 2.725
2025-11-09 08:00 | 1762693200 | 1 | 0.0889 | 0.178 | 152.27 | 91.96 | 1.573
2025-11-09 09:00 | 1762696800 | 1 | 0.1139 | 0.228 | 143.74 | 88.98 | 1.826
2025-11-09 10:00 | 1762700400 | 1 | 0.1667 | 0.392 | 130.41 | 84.12 | 2.657
2025-11-09 11:00 | 1762704000 | 1 | 0.0889 | 0.179 | 163.68 | 93.96 | 1.825
2025-11-09 12:00 | 1762707600 | 1 | 0.0889 | 0.182 | 158.39 | 91.6 | 1.781
2025-11-09 13:00 | 1762711200 | 1 | 0.0889 | 0.178 | 157.9 | 93.66 | 1.68
2025-11-09 14:00 | 1762714800 | 1 | 0.4944 | 0.988 | 160.76 | 122.39 | 5.557
2025-11-09 15:00 | 1762718400 | 1 | 0.7639 | 1.531 | 138.68 | 119.49 | 4.303
2025-11-09 16:00 | 1762722000 | 1 | 0.5972 | 1.201 | 138.3 | 117.93 | 3.584
2025-11-09 17:00 | 1762725600 | 1 | 0.4139 | 0.84 | 137.12 | 112.98 | 2.96
2025-11-09 18:00 | 1762729200 | 1 | 0 | 0 |  |  | 0
2025-11-09 19:00 | 1762732800 | 1 | 0.0833 | 0.169 | 143.69 | 80.48 | 1.569
2025-11-09 20:00 | 1762736400 | 1 | 0.0889 | 0.178 | 143.12 | 87.13 | 1.464
2025-11-09 21:00 | 1762740000 | 1 | 0.0889 | 0.179 | 142.23 | 89.52 | 1.383
2025-11-09 22:00 | 1762743600 | 1 | 0.0889 | 0.179 | 141.63 | 90 | 1.352
2025-11-09 23:00 | 1762747200 | 1 | 0.0944 | 0.189 | 141.15 | 91.94 | 1.365
2025-11-10 00:00 | 1762750800 | 1 | 0.1833 | 0.366 | 138.68 | 90.06 | 2.606
2025-11-10 01:00 | 1762754400 | 1 | 0.2 | 0.402 | 134.56 | 95.24 | 2.314
2025-11-10 02:00 | 1762758000 | 1 | 0.25 | 0.49 | 130.05 | 95.32 | 2.496
2025-11-10 03:00 | 1762761600 | 1 | 0.2556 | 0.484 | 136.6 | 94.41 | 2.992
2025-11-10 04:00 | 1762765200 | 1 | 0.1139 | 0.227 | 135.18 | 97 | 1.273
2025-11-10 05:00 | 1762768800 | 1 | 0.1889 | 0.382 | 133.32 | 93.5 | 2.229
2025-11-10 06:00 | 1762772400 | 1 | 0.1944 | 0.39 | 128.75 | 93.28 | 2.028
2025-11-10 07:00 | 1762776000 | 1 | 0.2528 | 0.516 | 134.42 | 93.3 | 3.111
2025-11-10 08:00 | 1762779600 | 1 | 0.0944 | 0.191 | 146.55 | 95.33 | 1.426
2025-11-10 09:00 | 1762783200 | 1 | 0.0889 | 0.179 | 143.92 | 92.72 | 1.346
2025-11-10 10:00 | 1762786800 | 1 | 0.1833 | 0.368 | 132.64 | 90.88 | 2.25
2025-11-10 11:00 | 1762790400 | 1 | 0.0944 | 0.189 | 139.34 | 91.34 | 1.332
2025-11-10 12:00 | 1762794000 | 1 | 0.0889 | 0.185 | 138.38 | 89.8 | 1.303
2025-11-10 13:00 | 1762797600 | 1 | 0.1889 | 0.384 | 137.84 | 91.2 | 2.623
2025-11-10 14:00 | 1762801200 | 1 | 0.0889 | 0.179 | 136.94 | 90.47 | 1.214
2025-11-10 15:00 | 1762804800 | 1 | 0.0944 | 0.189 | 135.85 | 88.3 | 1.32
2025-11-10 16:00 | 1762808400 | 1 | 0.0889 | 0.178 | 134.19 | 87.23 | 1.226
2025-11-10 17:00 | 1762812000 | 1 | 0.1722 | 0.344 | 131.48 | 86.71 | 2.259
2025-11-10 18:00 | 1762815600 | 1 | 0.0833 | 0.168 | 119.84 | 83.43 | 0.895
2025-11-10 19:00 | 1762819200 | 1 | 0.0889 | 0.181 | 133.38 | 85.63 | 1.265
2025-11-10 20:00 | 1762822800 | 1 | 0.1583 | 0.319 | 131.94 | 86.98 | 2.105
2025-11-10 21:00 | 1762826400 | 1 | 0.1194 | 0.24 | 133.31 | 92.62 | 1.433
2025-11-10 22:00 | 1762830000 | 1 | 0.1944 | 0.392 | 131.92 | 92.14 | 2.277
2025-11-10 23:00 | 1762833600 | 1 | 0.2417 | 0.531 | 105.03 | 83.65 | 1.662
2025-11-11 00:00 | 1762837200 | 1 | 0.2056 | 0.412 | 119.3 | 93.26 | 1.573
2025-11-11 01:00 | 1762840800 | 1 | 0.2056 | 0.425 | 125.15 | 94.07 | 1.917
2025-11-11 02:00 | 1762844400 | 1 | 0.1889 | 0.38 | 123.23 | 91.48 | 1.77
2025-11-11 03:00 | 1762848000 | 1 | 0.225 | 0.473 | 123.48 | 87.83 | 2.471
2025-11-11 04:00 | 1762851600 | 1 | 0.1944 | 0.389 | 122.68 | 91.08 | 1.803
2025-11-11 05:00 | 1762855200 | 1 | 0.1639 | 0.359 | 134.75 | 89.39 | 2.385
2025-11-11 06:00 | 1762858800 | 1 | 0.1389 | 0.308 | 155.02 | 95.91 | 2.67
2025-11-11 07:00 | 1762862400 | 1 | 0.0889 | 0.177 | 145.22 | 92.91 | 1.357
2025-11-11 08:00 | 1762866000 | 1 | 0.0889 | 0.178 | 140.64 | 91.46 | 1.281
2025-11-11 09:00 | 1762869600 | 1 | 0.2611 | 0.485 | 141.19 | 89.55 | 3.672
2025-11-11 10:00 | 1762873200 | 1 | 0.0833 | 0.17 | 157.62 | 92.44 | 1.624
2025-11-11 11:00 | 1762876800 | 1 | 0.1 | 0.199 | 155.34 | 75.71 | 2.322
2025-11-11 12:00 | 1762880400 | 1 | 0.0028 | 0.006 | 108.37 | 84.4 | 0.02
2025-11-11 13:00 | 1762884000 | 1 | 0.1694 | 0.34 | 143.54 | 90.35 | 2.646
2025-11-11 14:00 | 1762887600 | 1 | 0.0889 | 0.178 | 154.23 | 93.08 | 1.595
2025-11-11 15:00 | 1762891200 | 1 | 0.0889 | 0.179 | 153.36 | 94 | 1.561
2025-11-11 16:00 | 1762894800 | 1 | 0.175 | 0.356 | 153.16 | 94.69 | 3.051
2025-11-11 17:00 | 1762898400 | 1 | 0.0917 | 0.184 | 157.43 | 98.02 | 1.604
2025-11-11 18:00 | 1762902000 | 1 | 0.1167 | 0.225 | 157.65 | 92.74 | 2.132
2025-11-11 19:00 | 1762905600 | 1 | 0.1833 | 0.368 | 154.02 | 96.73 | 3.092
2025-11-11 20:00 | 1762909200 | 1 | 0.125 | 0.249 | 149.47 | 95.39 | 1.976
2025-11-11 21:00 | 1762912800 | 1 | 0.2 | 0.415 | 146.9 | 95.3 | 3.131
2025-11-11 22:00 | 1762916400 | 1 | 0.2972 | 0.598 | 137.35 | 99.88 | 3.284
2025-11-11 23:00 | 1762920000 | 1 | 0.3028 | 0.695 | 139.85 | 103.57 | 3.689
2025-11-12 00:00 | 1762923600 | 0.9972 | 0.3538 | 0.709 | 137.79 | 106.21 | 3.273
2025-11-12 01:00 | 1762927200 | 1 | 0.3028 | 0.606 | 150.6 | 113.12 | 3.326
2025-11-12 02:00 | 1762930800 | 1 | 0.2583 | 0.569 | 149.99 | 103.92 | 3.843
2025-11-12 03:00 | 1762934400 | 1 | 0.2222 | 0.445 | 148.19 | 106.47 | 2.721
2025-11-12 04:00 | 1762938000 | 1 | 0.3361 | 0.654 | 148.2 | 100.93 | 4.532
2025-11-12 05:00 | 1762941600 | 1 | 0.1417 | 0.282 | 163.46 | 111.83 | 2.135
2025-11-12 06:00 | 1762945200 | 1 | 0.2167 | 0.433 | 146.01 | 103.78 | 2.679
2025-11-12 07:00 | 1762948800 | 1 | 0.2167 | 0.488 | 165.75 | 101.72 | 4.576
2025-11-12 08:00 | 1762952400 | 1 | 0.1 | 0.202 | 163.5 | 103.03 | 1.79
2025-11-12 09:00 | 1762956000 | 1 | 0.1694 | 0.343 | 160.82 | 95.27 | 3.291
2025-11-12 10:00 | 1762959600 | 1 | 0.0139 | 0.028 | 166.54 | 114.46 | 0.213
2025-11-12 11:00 | 1762963200 | 1 | 0.1194 | 0.251 | 160.37 | 83.53 | 2.825
2025-11-12 12:00 | 1762966800 | 1 | 0.0778 | 0.161 | 154.52 | 82.33 | 1.689
2025-11-12 13:00 | 1762970400 | 1 | 0 | 0 |  |  | 0
2025-11-12 14:00 | 1762974000 | 1 | 0.0833 | 0.167 | 148.63 | 83.16 | 1.599
2025-11-12 15:00 | 1762977600 | 1 | 0.125 | 0.25 | 145.32 | 86.62 | 2.147
2025-11-12 16:00 | 1762981200 | 1 | 0.1306 | 0.264 | 141.3 | 92.03 | 1.901
2025-11-12 17:00 | 1762984800 | 1 | 0.0944 | 0.189 | 124.57 | 87.32 | 1.031
2025-11-12 18:00 | 1762988400 | 1 | 0.1528 | 0.307 | 154.63 | 92.13 | 2.809
2025-11-12 19:00 | 1762992000 | 1 | 0.1194 | 0.24 | 152.6 | 96.48 | 1.976
2025-11-12 20:00 | 1762995600 | 1 | 0.1194 | 0.262 | 152.83 | 89.82 | 2.422
2025-11-12 21:00 | 1762999200 | 1 | 0.1833 | 0.367 | 149.86 | 93.5 | 3.034
2025-11-12 22:00 | 1763002800 | 1 | 0.0889 | 0.179 | 148.62 | 94.43 | 1.418
2025-11-12 23:00 | 1763006400 | 1 | 0.1778 | 0.358 | 139.96 | 94.23 | 2.398
2025-11-13 00:00 | 1763010000 | 1 | 0.2528 | 0.49 | 138.11 | 92.06 | 3.31
2025-11-13 01:00 | 1763013600 | 1 | 0.0944 | 0.19 | 140.73 | 95.84 | 1.247
2025-11-13 02:00 | 1763017200 | 1 | 0.1944 | 0.389 | 137.75 | 95.65 | 2.401
2025-11-13 03:00 | 1763020800 | 1 | 0.2 | 0.398 | 133.16 | 96.82 | 2.118
2025-11-13 04:00 | 1763024400 | 1 | 0.1972 | 0.473 | 149.08 | 94.94 | 3.749
2025-11-13 05:00 | 1763028000 | 1 | 0.0944 | 0.194 | 146.96 | 96.91 | 1.418
2025-11-13 06:00 | 1763031600 | 1 | 0.1889 | 0.38 | 143.37 | 95.83 | 2.642
2025-11-13 07:00 | 1763035200 | 1 | 0.1722 | 0.428 | 142.4 | 90.31 | 3.264
2025-11-13 08:00 | 1763038800 | 1 | 0.1139 | 0.228 | 140.32 | 96.88 | 1.454
2025-11-13 09:00 | 1763042400 | 1 | 0.2 | 0.405 | 130.55 | 93.97 | 2.17
2025-11-13 10:00 | 1763046000 | 1 | 0.2 | 0.407 | 138.19 | 96.66 | 2.47
2025-11-13 11:00 | 1763049600 | 1 | 0.1139 | 0.229 | 135.16 | 95.34 | 1.337
2025-11-13 12:00 | 1763053200 | 1 | 0.1861 | 0.376 | 137.27 | 95.94 | 2.269
2025-11-13 13:00 | 1763056800 | 1 | 0.1889 | 0.381 | 133.34 | 92.28 | 2.287
2025-11-13 14:00 | 1763060400 | 1 | 0.175 | 0.348 | 134.03 | 93.53 | 2.065
2025-11-13 15:00 | 1763064000 | 1 | 0.125 | 0.249 | 133.69 | 99.69 | 1.242
2025-11-13 16:00 | 1763067600 | 1 | 0.1889 | 0.382 | 135.49 | 93.5 | 2.342
2025-11-13 17:00 | 1763071200 | 1 | 0.1389 | 0.258 | 143.51 | 89.73 | 2.019
2025-11-13 18:00 | 1763074800 | 1 | 0.1944 | 0.387 | 145.28 | 92.91 | 2.959
2025-11-13 19:00 | 1763078400 | 1 | 0.0889 | 0.179 | 141.83 | 89.7 | 1.362
2025-11-13 20:00 | 1763082000 | 1 | 0.1139 | 0.233 | 139.52 | 89.96 | 1.68
2025-11-13 21:00 | 1763085600 | 1 | 0.1639 | 0.329 | 140.44 | 95.31 | 2.178
2025-11-13 22:00 | 1763089200 | 1 | 0.2556 | 0.476 | 135.49 | 91.64 | 3.048
2025-11-13 23:00 | 1763092800 | 1 | 0.1889 | 0.38 | 139.13 | 95.47 | 2.431
2025-11-14 00:00 | 1763096400 | 1 | 0.1139 | 0.231 | 134.8 | 95.07 | 1.337
2025-11-14 01:00 | 1763100000 | 1 | 0.2444 | 0.461 | 134.99 | 93.36 | 2.8
2025-11-14 02:00 | 1763103600 | 1 | 0.3056 | 0.613 | 132.83 | 97.93 | 3.136
2025-11-14 03:00 | 1763107200 | 1 | 0.1944 | 0.39 | 152.37 | 103.21 | 2.807
2025-11-14 04:00 | 1763110800 | 1 | 0.1389 | 0.289 | 149.76 | 95.76 | 2.286
2025-11-14 05:00 | 1763114400 | 1 | 0.2 | 0.4 | 145.05 | 100.17 | 2.632
2025-11-14 06:00 | 1763118000 | 1 | 0.2611 | 0.5 | 142.17 | 96.8 | 3.321
2025-11-14 07:00 | 1763121600 | 1 | 0.2111 | 0.424 | 143.66 | 101.26 | 2.636
2025-11-14 08:00 | 1763125200 | 1 | 0.2 | 0.405 | 147.43 | 101.48 | 2.712
2025-11-14 09:00 | 1763128800 | 1 | 0.1611 | 0.291 | 147.87 | 93.35 | 2.322
2025-11-14 10:00 | 1763132400 | 1 | 0.0778 | 0.156 | 147.48 | 89.05 | 1.332
2025-11-14 11:00 | 1763136000 | 1 | 0.1889 | 0.384 | 141.62 | 91.76 | 2.8
2025-11-14 12:00 | 1763139600 | 1 | 0.0944 | 0.194 | 142.59 | 93.36 | 1.401
2025-11-14 13:00 | 1763143200 | 1 | 0.1778 | 0.357 | 139.8 | 91.54 | 2.519
2025-11-14 14:00 | 1763146800 | 1 | 0.0972 | 0.196 | 106.99 | 87.59 | 0.557
2025-11-14 15:00 | 1763150400 | 1 | 0.2083 | 0.423 | 145.45 | 98.52 | 2.898
2025-11-14 16:00 | 1763154000 | 1 | 0.1889 | 0.384 | 136.4 | 94.41 | 2.353
2025-11-14 17:00 | 1763157600 | 1 | 0.1028 | 0.27 | 136.58 | 82.71 | 2.135
2025-11-14 18:00 | 1763161200 | 1 | 0.1833 | 0.368 | 147.47 | 94.97 | 2.833
2025-11-14 19:00 | 1763164800 | 1 | 0.0889 | 0.178 | 142.16 | 94.32 | 1.248
2025-11-14 20:00 | 1763168400 | 1 | 0.1889 | 0.383 | 133.34 | 93.99 | 2.201
2025-11-14 21:00 | 1763172000 | 1 | 0.2139 | 0.482 | 141 | 92.17 | 3.451
2025-11-14 22:00 | 1763175600 | 1 | 0.0889 | 0.18 | 152.38 | 96.17 | 1.484
2025-11-14 23:00 | 1763179200 | 1 | 0.1778 | 0.357 | 151.14 | 95.5 | 2.911
2025-11-15 00:00 | 1763182800 | 1 | 0.1528 | 0.281 | 152.61 | 93.64 | 2.427
2025-11-15 01:00 | 1763186400 | 1 | 0.1944 | 0.39 | 149.22 | 97.97 | 2.927
2025-11-15 02:00 | 1763190000 | 1 | 0.1583 | 0.318 | 145.37 | 97.4 | 2.236
2025-11-15 03:00 | 1763193600 | 1 | 0.2028 | 0.378 | 145.3 | 96.94 | 2.667
2025-11-15 04:00 | 1763197200 | 1 | 0.1944 | 0.389 | 162.34 | 101.85 | 3.448
2025-11-15 05:00 | 1763200800 | 1 | 0.1306 | 0.264 | 156.62 | 98.91 | 2.227
2025-11-15 06:00 | 1763204400 | 1 | 0.1583 | 0.38 | 159.6 | 96.91 | 3.474
2025-11-15 07:00 | 1763208000 | 1 | 0.2 | 0.4 | 156.23 | 101.45 | 3.209
2025-11-15 08:00 | 1763211600 | 1 | 0.1 | 0.21 | 153.26 | 100.8 | 1.613
2025-11-15 09:00 | 1763215200 | 1 | 0.2028 | 0.451 | 136.88 | 92.14 | 2.96
2025-11-15 10:00 | 1763218800 | 1 | 0 | 0 |  |  | 0
2025-11-15 11:00 | 1763222400 | 1 | 0.0833 | 0.167 | 142.05 | 79.23 | 1.538
2025-11-15 12:00 | 1763226000 | 1 | 0.0889 | 0.177 | 143.33 | 88.28 | 1.428
2025-11-15 13:00 | 1763229600 | 1 | 0 | 0 |  |  | 0
2025-11-15 14:00 | 1763233200 | 1 | 0.0833 | 0.17 | 131.13 | 79.25 | 1.289
2025-11-15 15:00 | 1763236800 | 1 | 0.1833 | 0.368 | 148.11 | 92.54 | 2.999
2025-11-15 16:00 | 1763240400 | 1 | 0.0944 | 0.191 | 163.98 | 100.62 | 1.775
2025-11-15 17:00 | 1763244000 | 1 | 0.1306 | 0.262 | 159.99 | 94.21 | 2.525
2025-11-15 18:00 | 1763247600 | 1 | 0.2083 | 0.386 | 164.56 | 96.92 | 3.817
2025-11-15 19:00 | 1763251200 | 1 | 0.0944 | 0.189 | 160.49 | 99.06 | 1.7
2025-11-15 20:00 | 1763254800 | 1 | 0.1944 | 0.388 | 156.87 | 98.29 | 3.331
2025-11-15 21:00 | 1763258400 | 1 | 0.1917 | 0.359 | 150.47 | 92.14 | 3.054
2025-11-15 22:00 | 1763262000 | 1 | 0.1583 | 0.317 | 158.81 | 106.64 | 2.42
2025-11-15 23:00 | 1763265600 | 1 | 0.1889 | 0.379 | 155.9 | 100.71 | 3.068
2025-11-16 00:00 | 1763269200 | 1 | 0.1528 | 0.291 | 157.3 | 98 | 2.526
2025-11-16 01:00 | 1763272800 | 1 | 0.1944 | 0.392 | 150.05 | 98.22 | 2.973
2025-11-16 02:00 | 1763276400 | 1 | 0.2111 | 0.426 | 151.13 | 103.04 | 2.993
2025-11-16 03:00 | 1763280000 | 1 | 0.2778 | 0.527 | 137.13 | 97.55 | 3.049
2025-11-16 04:00 | 1763283600 | 1 | 0.2972 | 0.594 | 136.92 | 103.27 | 2.931
2025-11-16 05:00 | 1763287200 | 1 | 0.3917 | 0.748 | 135.75 | 103.32 | 3.557
2025-11-16 06:00 | 1763290800 | 1 | 0.2333 | 0.466 | 140.22 | 106.13 | 2.326
2025-11-16 07:00 | 1763294400 | 1 | 0.3444 | 0.695 | 138.97 | 104.5 | 3.506
2025-11-16 08:00 | 1763298000 | 1 | 0.2917 | 0.556 | 137.75 | 99.89 | 3.083
2025-11-16 09:00 | 1763301600 | 1 | 0.2222 | 0.444 | 133.8 | 101.51 | 2.101
2025-11-16 10:00 | 1763305200 | 1 | 0.3083 | 0.627 | 125.7 | 96.94 | 2.644
2025-11-16 11:00 | 1763308800 | 1 | 0.1861 | 0.389 | 149.78 | 102.65 | 2.676
2025-11-16 12:00 | 1763312400 | 1 | 0.1861 | 0.373 | 149.75 | 99.78 | 2.731
2025-11-16 13:00 | 1763316000 | 1 | 0.6667 | 1.335 | 150.82 | 124.2 | 5.208
2025-11-16 14:00 | 1763319600 | 1 | 0.0917 | 0.184 | 158.32 | 100.65 | 1.553
2025-11-16 15:00 | 1763323200 | 1 | 0.2167 | 0.434 | 143.52 | 99.13 | 2.825
2025-11-16 16:00 | 1763326800 | 1 | 0.2861 | 0.581 | 133.22 | 104.07 | 2.473
2025-11-16 17:00 | 1763330400 | 1 | 0.3556 | 0.71 | 148.21 | 111.25 | 3.845
2025-11-16 18:00 | 1763334000 | 1 | 0.2222 | 0.445 | 143.04 | 106.13 | 2.408
2025-11-16 19:00 | 1763337600 | 1 | 0.2222 | 0.445 | 137.46 | 104.37 | 2.158
2025-11-16 20:00 | 1763341200 | 1 | 0.3667 | 0.735 | 133.53 | 104.35 | 3.144
2025-11-16 21:00 | 1763344800 | 1 | 0.2444 | 0.494 | 132.02 | 103.9 | 2.038
2025-11-16 22:00 | 1763348400 | 1 | 0.2083 | 0.419 | 165.69 | 108.44 | 3.504
2025-11-16 23:00 | 1763352000 | 1 | 0.2028 | 0.407 | 163.99 | 105.38 | 3.494
2025-11-17 00:00 | 1763355600 | 1 | 0.1056 | 0.212 | 164.4 | 107.26 | 1.771
2025-11-17 01:00 | 1763359200 | 1 | 0.2111 | 0.423 | 160.7 | 106.52 | 3.358
2025-11-17 02:00 | 1763362800 | 1 | 0.2 | 0.4 | 157.3 | 104.68 | 3.085
2025-11-17 03:00 | 1763366400 | 1 | 0.2167 | 0.433 | 142.97 | 105.22 | 2.392
2025-11-17 04:00 | 1763370000 | 1 | 0.2278 | 0.456 | 163.4 | 106.85 | 3.78
2025-11-17 05:00 | 1763373600 | 1 | 0.2194 | 0.439 | 161.94 | 107.7 | 3.491
2025-11-17 06:00 | 1763377200 | 1 | 0.2111 | 0.421 | 161.37 | 110.36 | 3.145
2025-11-17 07:00 | 1763380800 | 1 | 0.2639 | 0.533 | 147.66 | 106.25 | 3.232
2025-11-17 08:00 | 1763384400 | 1 | 0.3083 | 0.619 | 155.83 | 112.83 | 3.901
2025-11-17 09:00 | 1763388000 | 1 | 0.2222 | 0.446 | 152.78 | 109.56 | 2.822
2025-11-17 10:00 | 1763391600 | 1 | 0.2056 | 0.41 | 151.38 | 105.79 | 2.738
2025-11-17 11:00 | 1763395200 | 1 | 0.2056 | 0.411 | 149.12 | 103.82 | 2.727
2025-11-17 12:00 | 1763398800 | 1 | 0.2056 | 0.416 | 138.46 | 100.43 | 2.299
2025-11-17 13:00 | 1763402400 | 1 | 0.2222 | 0.451 | 141.72 | 102.71 | 2.566
2025-11-17 14:00 | 1763406000 | 1 | 0.2167 | 0.435 | 140.81 | 104.15 | 2.335
2025-11-17 15:00 | 1763409600 | 1 | 0.325 | 0.655 | 144.62 | 105.6 | 3.743
2025-11-17 16:00 | 1763413200 | 1 | 0.2472 | 0.499 | 149.25 | 109.66 | 2.887
2025-11-17 17:00 | 1763416800 | 1 | 0.2167 | 0.434 | 147.98 | 105.84 | 2.68
2025-11-17 18:00 | 1763420400 | 1 | 0.2306 | 0.459 | 147 | 106.94 | 2.694
2025-11-17 19:00 | 1763424000 | 0.9528 | 0.2012 | 0.401 | 134.69 | 102.45 | 1.806
2025-11-17 20:00 | 1763427600 | 1 | 0.3139 | 0.629 | 137.71 | 109.66 | 2.587
2025-11-17 21:00 | 1763431200 | 1 | 0.4111 | 0.838 | 134.22 | 106.01 | 3.45
2025-11-17 22:00 | 1763434800 | 1 | 0.2917 | 0.591 | 133.24 | 105.44 | 2.406
2025-11-17 23:00 | 1763438400 | 1 | 0.3861 | 0.774 | 137.63 | 108.65 | 3.285
2025-11-18 00:00 | 1763442000 | 1 | 0.2444 | 0.491 | 154.24 | 111.4 | 3.078
2025-11-18 01:00 | 1763445600 | 1 | 0.2083 | 0.416 | 153.75 | 106.69 | 2.867
2025-11-18 02:00 | 1763449200 | 1 | 0.2056 | 0.41 | 152.49 | 105.63 | 2.814
2025-11-18 03:00 | 1763452800 | 1 | 0.2139 | 0.428 | 147.34 | 104.75 | 2.674
2025-11-18 04:00 | 1763456400 | 1 | 0.2639 | 0.527 | 139.2 | 101.65 | 2.898
2025-11-18 05:00 | 1763460000 | 1 | 0.2556 | 0.513 | 143.63 | 103.73 | 2.997
2025-11-18 06:00 | 1763463600 | 1 | 0.2611 | 0.533 | 142.57 | 106.15 | 2.826
2025-11-18 07:00 | 1763467200 | 1 | 0.2333 | 0.463 | 139.85 | 105.4 | 2.337
2025-11-18 08:00 | 1763470800 | 1 | 0.3361 | 0.683 | 139.89 | 103.49 | 3.644
2025-11-18 09:00 | 1763474400 | 1 | 0.1389 | 0.283 | 154.69 | 110.6 | 1.823
2025-11-18 10:00 | 1763478000 | 1 | 0.0889 | 0.176 | 152.29 | 95.14 | 1.475
2025-11-18 11:00 | 1763481600 | 1 | 0.075 | 0.151 | 147.62 | 81 | 1.472
2025-11-18 12:00 | 1763485200 | 1 | 0.0917 | 0.184 | 149.62 | 90.55 | 1.589
2025-11-18 13:00 | 1763488800 | 1 | 0 | 0 |  |  | 0
2025-11-18 14:00 | 1763492400 | 1 | 0.1944 | 0.394 | 146.45 | 90.53 | 3.21
2025-11-18 15:00 | 1763496000 | 1 | 0.0861 | 0.173 | 146.87 | 94.5 | 1.327
2025-11-18 16:00 | 1763499600 | 1 | 0.15 | 0.274 | 142.96 | 85.75 | 2.293
2025-11-18 17:00 | 1763503200 | 1 | 0.2056 | 0.412 | 135.38 | 93.46 | 2.533
2025-11-18 18:00 | 1763506800 | 1 | 0.2028 | 0.405 | 160.34 | 104.55 | 3.31
2025-11-18 19:00 | 1763510400 | 1 | 0.175 | 0.356 | 157.54 | 99.74 | 2.999
2025-11-18 20:00 | 1763514000 | 1 | 0.1278 | 0.257 | 158.39 | 105.92 | 1.968
2025-11-18 21:00 | 1763517600 | 1 | 0.1972 | 0.394 | 149.4 | 102.69 | 2.696
2025-11-18 22:00 | 1763521200 | 1 | 0.2028 | 0.406 | 149.89 | 103.27 | 2.774
2025-11-18 23:00 | 1763524800 | 1 | 0.2056 | 0.413 | 141.86 | 99.65 | 2.554
2025-11-19 00:00 | 1763528400 | 0.9972 | 0.1922 | 0.386 | 140.31 | 98.48 | 2.362
2025-11-19 01:00 | 1763532000 | 1 | 0.1417 | 0.287 | 155.8 | 105.34 | 2.105
2025-11-19 02:00 | 1763535600 | 1 | 0.1722 | 0.344 | 151.11 | 101.85 | 2.484
2025-11-19 03:00 | 1763539200 | 1 | 0.2 | 0.399 | 145.55 | 100.35 | 2.638
2025-11-19 04:00 | 1763542800 | 1 | 0.2056 | 0.41 | 149.53 | 102.6 | 2.814
2025-11-19 05:00 | 1763546400 | 1 | 0.2 | 0.403 | 152.71 | 102.99 | 2.94
2025-11-19 06:00 | 1763550000 | 1 | 0.2 | 0.482 | 145.65 | 96.05 | 3.506
2025-11-19 07:00 | 1763553600 | 1 | 0.1611 | 0.319 | 143.77 | 98.32 | 2.124
2025-11-19 08:00 | 1763557200 | 1 | 0.1556 | 0.311 | 143.23 | 103.98 | 1.787
2025-11-19 09:00 | 1763560800 | 1 | 0.2111 | 0.423 | 148.61 | 102.45 | 2.861
2025-11-19 10:00 | 1763564400 | 1 | 0 | 0 |  |  | 0
2025-11-19 11:00 | 1763568000 | 1 | 0 | 0 |  |  | 0
2025-11-19 12:00 | 1763571600 | 1 | 0 | 0 |  |  | 0
2025-11-19 13:00 | 1763575200 | 1 | 0 | 0 |  |  | 0
2025-11-19 14:00 | 1763578800 | 1 | 0.0306 | 0.066 | 126.25 | 66.56 | 0.582
2025-11-19 15:00 | 1763582400 | 1 | 0.1833 | 0.368 | 147.7 | 88.37 | 3.198
2025-11-19 16:00 | 1763586000 | 1 | 0.0917 | 0.186 | 155.15 | 94.23 | 1.661
2025-11-19 17:00 | 1763589600 | 1 | 0.0917 | 0.183 | 154.05 | 94.68 | 1.59
2025-11-19 18:00 | 1763593200 | 1 | 0.175 | 0.356 | 152.86 | 93.65 | 3.089
2025-11-19 19:00 | 1763596800 | 1 | 0.0944 | 0.192 | 150.93 | 92.98 | 1.623
2025-11-19 20:00 | 1763600400 | 1 | 0.0917 | 0.184 | 149.77 | 93.71 | 1.508
2025-11-19 21:00 | 1763604000 | 1 | 0.2 | 0.396 | 143.34 | 96.21 | 2.736
2025-11-19 22:00 | 1763607600 | 1 | 0.2028 | 0.406 | 159.87 | 102.7 | 3.402
2025-11-19 23:00 | 1763611200 | 1 | 0.0972 | 0.192 | 159.22 | 101.57 | 1.623
2025-11-20 00:00 | 1763614800 | 1 | 0.1944 | 0.385 | 159.2 | 101.59 | 3.254
2025-11-20 01:00 | 1763618400 | 1 | 0.1528 | 0.306 | 155.76 | 99.72 | 2.499
2025-11-20 02:00 | 1763622000 | 1 | 0.15 | 0.296 | 156.66 | 104.6 | 2.252
2025-11-20 03:00 | 1763625600 | 1 | 0.1972 | 0.399 | 150.42 | 100.71 | 2.9
2025-11-20 04:00 | 1763629200 | 1 | 0.2694 | 0.523 | 156.84 | 99.28 | 4.413
2025-11-20 05:00 | 1763632800 | 1 | 0.1028 | 0.204 | 163.9 | 105.56 | 1.746
2025-11-20 06:00 | 1763636400 | 1 | 0.225 | 0.447 | 149.66 | 99.77 | 3.268
2025-11-20 07:00 | 1763640000 | 1 | 0.2028 | 0.413 | 154.27 | 102.82 | 3.1
2025-11-20 08:00 | 1763643600 | 1 | 0.2028 | 0.403 | 153.27 | 102.93 | 2.975
2025-11-20 09:00 | 1763647200 | 1 | 0.0944 | 0.19 | 159.9 | 101.69 | 1.618
2025-11-20 10:00 | 1763650800 | 1 | 0.0833 | 0.168 | 156.92 | 93.95 | 1.547
2025-11-20 13:00 | 1763661600 | 1 | 0.0778 | 0.156 | 147.98 | 76.63 | 1.63
2025-11-20 14:00 | 1763665200 | 1 | 0.0833 | 0.171 | 151.3 | 86.34 | 1.624
2025-11-20 15:00 | 1763668800 | 1 | 0.0944 | 0.19 | 140.48 | 90.37 | 1.398
2025-11-20 16:00 | 1763672400 | 1 | 0.1889 | 0.381 | 139.1 | 93.69 | 2.532
2025-11-20 17:00 | 1763676000 | 1 | 0.1889 | 0.384 | 138.4 | 96.08 | 2.371
2025-11-20 18:00 | 1763679600 | 1 | 0.2 | 0.393 | 137.22 | 96.61 | 2.336
2025-11-20 19:00 | 1763683200 | 1 | 0.2111 | 0.425 | 148.89 | 101.78 | 2.934
2025-11-20 20:00 | 1763686800 | 1 | 0.0972 | 0.195 | 164.3 | 104.76 | 1.703
2025-11-20 21:00 | 1763690400 | 1 | 0.2028 | 0.403 | 161.72 | 102.87 | 3.476
2025-11-20 22:00 | 1763694000 | 1 | 0.1056 | 0.294 | 157.15 | 93.42 | 2.741
2025-11-20 23:00 | 1763697600 | 1 | 0.1889 | 0.378 | 150.78 | 100.19 | 2.798
2025-11-21 00:00 | 1763701200 | 1 | 0.2944 | 0.591 | 127.02 | 97.57 | 2.547
2025-11-21 01:00 | 1763704800 | 1 | 0.3111 | 0.627 | 138.42 | 108.18 | 2.773
2025-11-21 02:00 | 1763708400 | 1 | 0.3083 | 0.592 | 140.21 | 102.23 | 3.295
2025-11-21 03:00 | 1763712000 | 1 | 0.3111 | 0.634 | 140.64 | 105.75 | 3.229
2025-11-21 04:00 | 1763715600 | 1 | 0.2667 | 0.539 | 149.75 | 108.89 | 3.218
2025-11-21 05:00 | 1763719200 | 1 | 0.2556 | 0.481 | 157.49 | 101.88 | 3.917
2025-11-21 06:00 | 1763722800 | 1 | 0.1167 | 0.234 | 150.47 | 104 | 1.592
2025-11-21 07:00 | 1763726400 | 1 | 0.2167 | 0.438 | 150.71 | 105.56 | 2.883
2025-11-21 08:00 | 1763730000 | 1 | 0.2278 | 0.458 | 139.65 | 103.86 | 2.402
2025-11-21 09:00 | 1763733600 | 1 | 0.2 | 0.4 | 160.56 | 103.63 | 3.337
2025-11-21 10:00 | 1763737200 | 1 | 0.1444 | 0.289 | 156.8 | 96.62 | 2.545
2025-11-21 11:00 | 1763740800 | 1 | 0.1278 | 0.256 | 158.09 | 99.69 | 2.195
2025-11-21 12:00 | 1763744400 | 1 | 0.0889 | 0.178 | 156.84 | 97.95 | 1.535
2025-11-21 13:00 | 1763748000 | 1 | 0.1778 | 0.356 | 153.71 | 96.34 | 2.991
2025-11-21 14:00 | 1763751600 | 1 | 0.0944 | 0.189 | 150.92 | 97.28 | 1.485
2025-11-21 15:00 | 1763755200 | 1 | 0.1889 | 0.377 | 143.68 | 95.45 | 2.661
2025-11-21 16:00 | 1763758800 | 1 | 0.0944 | 0.188 | 128.49 | 92.37 | 0.996
2025-11-21 17:00 | 1763762400 | 1 | 0.1889 | 0.378 | 152.42 | 97.17 | 3.063
2025-11-21 18:00 | 1763766000 | 1 | 0.0944 | 0.19 | 152.06 | 97.27 | 1.522
2025-11-21 19:00 | 1763769600 | 1 | 0.1778 | 0.359 | 150.7 | 94.51 | 2.956
2025-11-21 20:00 | 1763773200 | 1 | 0.0889 | 0.183 | 149.23 | 93.18 | 1.492
2025-11-21 21:00 | 1763776800 | 1 | 0.0944 | 0.189 | 148.41 | 93.86 | 1.51
2025-11-21 22:00 | 1763780400 | 1 | 0.2278 | 0.432 | 144.93 | 92.34 | 3.328
2025-11-21 23:00 | 1763784000 | 1 | 0.0944 | 0.19 | 133.27 | 91.2 | 1.169
2025-11-22 00:00 | 1763787600 | 1 | 0.1889 | 0.383 | 148.86 | 96.7 | 2.913
2025-11-22 01:00 | 1763791200 | 1 | 0.0944 | 0.19 | 147.21 | 96.15 | 1.422
2025-11-22 02:00 | 1763794800 | 1 | 0.1889 | 0.384 | 146.52 | 95.83 | 2.842
2025-11-22 03:00 | 1763798400 | 1 | 0.1722 | 0.345 | 145.56 | 95.08 | 2.553
2025-11-22 04:00 | 1763802000 | 1 | 0.1056 | 0.211 | 142.39 | 98.67 | 1.352
2025-11-22 05:00 | 1763805600 | 1 | 0.2389 | 0.469 | 134.23 | 92.58 | 2.862
2025-11-22 06:00 | 1763809200 | 1 | 0.2056 | 0.414 | 137.02 | 96.49 | 2.456
2025-11-22 07:00 | 1763812800 | 1 | 0.0944 | 0.191 | 137.06 | 96.94 | 1.122
2025-11-22 08:00 | 1763816400 | 1 | 0.1944 | 0.39 | 130.53 | 92.85 | 2.154
2025-11-22 09:00 | 1763820000 | 1 | 0.2111 | 0.429 | 124.76 | 94.08 | 1.93
2025-11-22 10:00 | 1763823600 | 1 | 0.0944 | 0.189 | 122.44 | 90.36 | 0.89
2025-11-22 11:00 | 1763827200 | 1 | 0.1 | 0.205 | 133.3 | 83.47 | 1.491
2025-11-22 12:00 | 1763830800 | 1 | 0.0944 | 0.19 | 134.4 | 91.26 | 1.2
2025-11-22 13:00 | 1763834400 | 1 | 0.0833 | 0.166 | 132.23 | 86.48 | 1.113
2025-11-22 14:00 | 1763838000 | 1 | 0.1944 | 0.394 | 132.68 | 91.46 | 2.381
2025-11-22 15:00 | 1763841600 | 1 | 0.2 | 0.401 | 132.4 | 96.01 | 2.138
2025-11-22 16:00 | 1763845200 | 1 | 0.2111 | 0.428 | 138.13 | 97.82 | 2.524
2025-11-22 17:00 | 1763848800 | 1 | 0.2 | 0.404 | 156.45 | 101.32 | 3.26
2025-11-22 18:00 | 1763852400 | 1 | 0.1 | 0.2 | 152.68 | 100.66 | 1.525
2025-11-22 19:00 | 1763856000 | 1 | 0.2056 | 0.416 | 151.7 | 100.98 | 3.094
2025-11-22 20:00 | 1763859600 | 1 | 0.1889 | 0.378 | 150.19 | 100.02 | 2.777
2025-11-22 21:00 | 1763863200 | 1 | 0.1889 | 0.377 | 146.26 | 102.79 | 2.403
2025-11-22 22:00 | 1763866800 | 1 | 0.3583 | 0.673 | 139.53 | 101.61 | 3.741
2025-11-22 23:00 | 1763870400 | 1 | 0.25 | 0.51 | 130.75 | 103.91 | 2.003
2025-11-23 00:00 | 1763874000 | 1 | 0.3667 | 0.742 | 136.11 | 105.18 | 3.354
2025-11-23 01:00 | 1763877600 | 1 | 0.25 | 0.504 | 133.04 | 104.24 | 2.127
2025-11-23 02:00 | 1763881200 | 1 | 0.3944 | 0.875 | 133.4 | 101.68 | 4.065
2025-11-23 03:00 | 1763884800 | 1 | 0.3833 | 0.773 | 129.88 | 104.04 | 2.925
2025-11-23 04:00 | 1763888400 | 1 | 0.2889 | 0.588 | 143.89 | 109.87 | 2.928
2025-11-23 05:00 | 1763892000 | 1 | 0.2278 | 0.46 | 157.13 | 110.17 | 3.155
2025-11-23 06:00 | 1763895600 | 1 | 0.2056 | 0.415 | 151.35 | 103.64 | 2.895
2025-11-23 07:00 | 1763899200 | 1 | 0.2389 | 0.552 | 149.24 | 100.11 | 3.952
2025-11-23 08:00 | 1763902800 | 1 | 0.2167 | 0.435 | 137.75 | 101.22 | 2.326
2025-11-23 09:00 | 1763906400 | 1 | 0.2111 | 0.422 | 151.89 | 105.02 | 2.896
2025-11-23 10:00 | 1763910000 | 1 | 0.1889 | 0.379 | 148.11 | 99.82 | 2.674
2025-11-23 11:00 | 1763913600 | 1 | 0.0833 | 0.167 | 163.31 | 92.3 | 1.743
2025-11-23 12:00 | 1763917200 | 1 | 0 | 0 |  |  | 0
2025-11-23 13:00 | 1763920800 | 1 | 0.0889 | 0.181 | 158.1 | 88.43 | 1.843
2025-11-23 14:00 | 1763924400 | 1 | 0.1361 | 0.272 | 154.86 | 87.24 | 2.699
2025-11-23 15:00 | 1763928000 | 1 | 0.1278 | 0.26 | 153.76 | 97.05 | 2.154
2025-11-23 16:00 | 1763931600 | 1 | 0.0944 | 0.189 | 151.21 | 95.91 | 1.531
2025-11-23 17:00 | 1763935200 | 1 | 0.1944 | 0.389 | 140.3 | 96.01 | 2.528
2025-11-23 18:00 | 1763938800 | 1 | 0.1556 | 0.313 | 165.57 | 100.76 | 2.975
2025-11-23 19:00 | 1763942400 | 1 | 0.1333 | 0.268 | 166.8 | 103.11 | 2.5
2025-11-23 20:00 | 1763946000 | 1 | 0.0944 | 0.189 | 165.3 | 99.79 | 1.813
2025-11-23 21:00 | 1763949600 | 1 | 0.0944 | 0.188 | 162.11 | 98.76 | 1.748
2025-11-23 22:00 | 1763953200 | 1 | 0.1833 | 0.367 | 159.73 | 97.69 | 3.34
2025-11-23 23:00 | 1763956800 | 1 | 0.0944 | 0.188 | 157.14 | 98.6 | 1.615
2025-11-24 00:00 | 1763960400 | 1 | 0.1889 | 0.378 | 144.35 | 98.39 | 2.546
2025-11-24 01:00 | 1763964000 | 1 | 0.1056 | 0.211 | 158.75 | 103.12 | 1.721
2025-11-24 02:00 | 1763967600 | 1 | 0.1944 | 0.39 | 155.54 | 100.8 | 3.13
2025-11-24 03:00 | 1763971200 | 1 | 0.1278 | 0.256 | 150.62 | 97.09 | 2.009
2025-11-24 04:00 | 1763974800 | 1 | 0.1556 | 0.316 | 152.88 | 100.99 | 2.407
2025-11-24 05:00 | 1763978400 | 1 | 0.2306 | 0.445 | 148.41 | 99.62 | 3.184
2025-11-24 06:00 | 1763982000 | 1 | 0.2111 | 0.425 | 150.7 | 100.32 | 3.136
2025-11-24 07:00 | 1763985600 | 1 | 0.1667 | 0.344 | 158.23 | 101.15 | 2.877
2025-11-24 08:00 | 1763989200 | 1 | 0.1222 | 0.245 | 158.57 | 104.04 | 1.961
2025-11-24 09:00 | 1763992800 | 1 | 0.1833 | 0.366 | 155.92 | 98.13 | 3.102
2025-11-24 10:00 | 1763996400 | 1 | 0 | 0 |  |  | 0
2025-11-24 11:00 | 1764000000 | 1 | 0.0889 | 0.182 | 151.01 | 87.03 | 1.694
2025-11-24 12:00 | 1764003600 | 1 | 0.0833 | 0.167 | 148.33 | 85.59 | 1.532
2025-11-24 13:00 | 1764007200 | 1 | 0.0861 | 0.173 | 142.41 | 84.76 | 1.458
2025-11-24 14:00 | 1764010800 | 1 | 0.0917 | 0.184 | 135.64 | 90.68 | 1.213
2025-11-24 15:00 | 1764014400 | 1 | 0.1944 | 0.39 | 143.04 | 94.88 | 2.752
2025-11-24 16:00 | 1764018000 | 1 | 0.0944 | 0.19 | 164.75 | 98.87 | 1.828
2025-11-24 17:00 | 1764021600 | 1 | 0.0889 | 0.183 | 163.01 | 95.75 | 1.788
2025-11-24 18:00 | 1764025200 | 1 | 0.0889 | 0.177 | 161.67 | 93.75 | 1.762
2025-11-24 19:00 | 1764028800 | 1 | 0.1667 | 0.333 | 160.13 | 93.27 | 3.266
2025-11-24 20:00 | 1764032400 | 1 | 0.7944 | 1.58 | 159.9 | 133.11 | 6.212
2025-11-24 21:00 | 1764036000 | 1 | 1 | 1.982 | 160.76 | 137.66 | 6.708
2025-11-24 22:00 | 1764039600 | 1 | 1 | 1.996 | 146.64 | 127.28 | 5.662
2025-11-24 23:00 | 1764043200 | 1 | 0.7778 | 1.556 | 155.03 | 131.85 | 5.282
2025-11-25 00:00 | 1764046800 | 1 | 0.625 | 1.254 | 135.59 | 118.63 | 3.113
2025-11-25 01:00 | 1764050400 | 1 | 0.6306 | 1.261 | 146.35 | 119.55 | 4.953
2025-11-25 02:00 | 1764054000 | 1 | 0.3583 | 0.721 | 149.15 | 116.4 | 3.454
2025-11-25 03:00 | 1764057600 | 1 | 0.325 | 0.652 | 150.07 | 117.43 | 3.116
2025-11-25 04:00 | 1764061200 | 1 | 0.3889 | 0.772 | 148.56 | 115.1 | 3.787
2025-11-25 05:00 | 1764064800 | 1 | 0.275 | 0.548 | 151.55 | 114.09 | 3.006
2025-11-25 06:00 | 1764068400 | 1 | 0.3083 | 0.618 | 157.33 | 113.7 | 3.952
2025-11-25 07:00 | 1764072000 | 1 | 0.2278 | 0.457 | 156.75 | 112.99 | 2.933
2025-11-25 08:00 | 1764075600 | 1 | 0.2222 | 0.443 | 155.76 | 111.98 | 2.844
2025-11-25 09:00 | 1764079200 | 1 | 0.3361 | 0.67 | 145.2 | 110.52 | 3.407
2025-11-25 10:00 | 1764082800 | 1 | 0.0139 | 0.033 | 121.96 | 116.14 | 0.029
2025-11-25 11:00 | 1764086400 | 1 | 0 | 0 |  |  | 0
2025-11-25 12:00 | 1764090000 | 1 | 0.1639 | 0.329 | 115.27 | 79.45 | 1.726
2025-11-25 13:00 | 1764093600 | 1 | 0.1889 | 0.378 | 127.56 | 93.07 | 1.909
2025-11-25 14:00 | 1764097200 | 1 | 0.1417 | 0.286 | 125.08 | 97.04 | 1.176
2025-11-25 15:00 | 1764100800 | 1 | 0.2028 | 0.413 | 144.95 | 96.34 | 2.933
2025-11-25 16:00 | 1764104400 | 1 | 0.1083 | 0.219 | 150.56 | 98.23 | 1.68
2025-11-25 17:00 | 1764108000 | 1 | 0.175 | 0.351 | 153.48 | 98.17 | 2.841
2025-11-25 18:00 | 1764111600 | 1 | 0.0889 | 0.178 | 148.73 | 88.72 | 1.567
2025-11-25 19:00 | 1764115200 | 1 | 0.0889 | 0.18 | 149.12 | 91.99 | 1.51
2025-11-25 20:00 | 1764118800 | 1 | 0.0889 | 0.18 | 148.23 | 93.45 | 1.441
2025-11-25 21:00 | 1764122400 | 1 | 0.1639 | 0.325 | 144.6 | 91.92 | 2.511
2025-11-25 22:00 | 1764126000 | 1 | 0.125 | 0.253 | 131.36 | 96.96 | 1.275
2025-11-25 23:00 | 1764129600 | 1 | 0.2111 | 0.421 | 137.01 | 97.83 | 2.417
2025-11-26 00:00 | 1764133200 | 0.9972 | 0.2006 | 0.406 | 137.19 | 98.27 | 2.307
2025-11-26 01:00 | 1764136800 | 1 | 0.2 | 0.402 | 135.07 | 97.61 | 2.209
2025-11-26 02:00 | 1764140400 | 1 | 0.2167 | 0.441 | 134.21 | 98.81 | 2.273
2025-11-26 03:00 | 1764144000 | 1 | 0.2167 | 0.438 | 130.75 | 99.2 | 2.023
2025-11-26 04:00 | 1764147600 | 1 | 0.2222 | 0.447 | 127.85 | 98.49 | 1.925
2025-11-26 05:00 | 1764151200 | 1 | 0.2222 | 0.45 | 126.51 | 97.95 | 1.883
2025-11-26 06:00 | 1764154800 | 1 | 0.1944 | 0.394 | 130.55 | 93.28 | 2.153
2025-11-26 07:00 | 1764158400 | 1 | 0.1417 | 0.287 | 128.5 | 92.09 | 1.524
2025-11-26 08:00 | 1764162000 | 1 | 0.2333 | 0.47 | 127.32 | 95.22 | 2.208
2025-11-26 09:00 | 1764165600 | 1 | 0.2278 | 0.457 | 141.43 | 97.56 | 2.936
2025-11-26 10:00 | 1764169200 | 1 | 0.1306 | 0.262 | 154.6 | 102.81 | 1.989
2025-11-26 11:00 | 1764172800 | 1 | 0.0944 | 0.19 | 151.24 | 94.67 | 1.574
2025-11-26 12:00 | 1764176400 | 1 | 0.0833 | 0.169 | 147.66 | 86.6 | 1.516
2025-11-26 13:00 | 1764180000 | 1 | 0.0917 | 0.183 | 147.46 | 89.94 | 1.542
2025-11-26 14:00 | 1764183600 | 1 | 0.0944 | 0.189 | 149.09 | 93.95 | 1.526
2025-11-26 15:00 | 1764187200 | 1 | 0.1111 | 0.222 | 149.57 | 100.97 | 1.583
2025-11-26 16:00 | 1764190800 | 1 | 0.0833 | 0.167 | 142.75 | 88.85 | 1.318
2025-11-26 17:00 | 1764194400 | 1 | 0.0889 | 0.179 | 138.38 | 88.54 | 1.305
2025-11-26 18:00 | 1764198000 | 1 | 0.175 | 0.352 | 130.89 | 86.36 | 2.294
2025-11-26 19:00 | 1764201600 | 1 | 0.0944 | 0.192 | 161.08 | 97.02 | 1.788
2025-11-26 20:00 | 1764205200 | 1 | 0.0889 | 0.179 | 158.19 | 93.98 | 1.68
2025-11-26 21:00 | 1764208800 | 1 | 0.0889 | 0.179 | 157.21 | 92.92 | 1.683
2025-11-26 22:00 | 1764212400 | 1 | 0.0889 | 0.183 | 155.68 | 92.58 | 1.679
2025-11-26 23:00 | 1764216000 | 1 | 0.0917 | 0.188 | 153.22 | 91.96 | 1.673
2025-11-27 00:00 | 1764219600 | 1 | 0.1694 | 0.34 | 151.77 | 93.69 | 2.893
2025-11-27 01:00 | 1764223200 | 1 | 0.0889 | 0.177 | 151.13 | 93.84 | 1.488
2025-11-27 02:00 | 1764226800 | 1 | 0.0889 | 0.18 | 145.64 | 92.34 | 1.404
2025-11-27 03:00 | 1764230400 | 1 | 0.0889 | 0.182 | 141.03 | 91.65 | 1.304
2025-11-27 04:00 | 1764234000 | 1 | 0.1944 | 0.39 | 134.15 | 93 | 2.353
2025-11-27 05:00 | 1764237600 | 1 | 0.1583 | 0.316 | 140.87 | 94.02 | 2.17
2025-11-27 06:00 | 1764241200 | 1 | 0.125 | 0.251 | 141.33 | 99.26 | 1.55
2025-11-27 07:00 | 1764244800 | 1 | 0.1944 | 0.389 | 139.3 | 96.28 | 2.45
2025-11-27 08:00 | 1764248400 | 1 | 0.0944 | 0.193 | 137.19 | 94.43 | 1.211
2025-11-27 09:00 | 1764252000 | 1 | 0.1944 | 0.396 | 133.88 | 94.61 | 2.268
2025-11-27 10:00 | 1764255600 | 1 | 0 | 0 |  |  | 0
2025-11-27 11:00 | 1764259200 | 1 | 0.0833 | 0.167 | 117.87 | 78.71 | 0.961
2025-11-27 12:00 | 1764262800 | 1 | 0.0861 | 0.173 | 160.76 | 87.83 | 1.853
2025-11-27 13:00 | 1764266400 | 1 | 0.0889 | 0.178 | 158.59 | 92.09 | 1.735
2025-11-27 14:00 | 1764270000 | 1 | 0.0833 | 0.164 | 155.43 | 90.59 | 1.562
2025-11-27 15:00 | 1764273600 | 1 | 0.1417 | 0.279 | 149.47 | 90.46 | 2.415
2025-11-27 16:00 | 1764277200 | 1 | 0.1306 | 0.262 | 138.84 | 94.42 | 1.707
2025-11-27 17:00 | 1764280800 | 1 | 0.1 | 0.201 | 162.73 | 99.21 | 1.869
2025-11-27 18:00 | 1764284400 | 1 | 0.1889 | 0.379 | 160.22 | 98.77 | 3.41
2025-11-27 19:00 | 1764288000 | 1 | 0.0944 | 0.189 | 159.28 | 99.53 | 1.654
2025-11-27 20:00 | 1764291600 | 1 | 0.1889 | 0.377 | 157.8 | 98.44 | 3.28
2025-11-27 21:00 | 1764295200 | 1 | 0.0944 | 0.188 | 155.85 | 97.27 | 1.613
2025-11-27 22:00 | 1764298800 | 1 | 0.0944 | 0.191 | 154.7 | 97.53 | 1.591
2025-11-27 23:00 | 1764302400 | 1 | 0.2 | 0.398 | 140.4 | 98.47 | 2.447
2025-11-28 00:00 | 1764306000 | 1 | 0.1944 | 0.392 | 155.82 | 100.85 | 3.154
2025-11-28 01:00 | 1764309600 | 1 | 0.0944 | 0.19 | 152.37 | 98.7 | 1.493
2025-11-28 02:00 | 1764313200 | 1 | 0.1944 | 0.39 | 152.17 | 99.28 | 3.022
2025-11-28 03:00 | 1764316800 | 1 | 0.0944 | 0.194 | 149.72 | 99.79 | 1.403
2025-11-28 04:00 | 1764320400 | 1 | 0.1944 | 0.387 | 148.05 | 99.14 | 2.777
2025-11-28 05:00 | 1764324000 | 1 | 0.2111 | 0.42 | 140.15 | 99.35 | 2.511
2025-11-28 06:00 | 1764327600 | 1 | 0.1583 | 0.315 | 155.09 | 101.31 | 2.483
2025-11-28 07:00 | 1764331200 | 1 | 0.1472 | 0.301 | 154.09 | 105.51 | 2.125
2025-11-28 08:00 | 1764334800 | 1 | 0.1944 | 0.388 | 153.16 | 100.82 | 2.977
2025-11-28 09:00 | 1764338400 | 1 | 0.125 | 0.249 | 150.26 | 99.24 | 1.858
2025-11-28 10:00 | 1764342000 | 1 | 0.175 | 0.35 | 152.64 | 101.66 | 2.615
2025-11-28 11:00 | 1764345600 | 1 | 0.1889 | 0.377 | 145.48 | 98.12 | 2.616
2025-11-28 12:00 | 1764349200 | 1 | 0.2167 | 0.435 | 134.13 | 99 | 2.241
2025-11-28 13:00 | 1764352800 | 1 | 0.3806 | 0.766 | 142.21 | 113.56 | 3.215
2025-11-28 14:00 | 1764356400 | 1 | 0.3778 | 0.759 | 129.82 | 104.6 | 2.804
2025-11-28 15:00 | 1764360000 | 1 | 0.4056 | 0.818 | 130.1 | 104.64 | 3.052
2025-11-28 16:00 | 1764363600 | 1 | 0.3139 | 0.633 | 140.11 | 111.02 | 2.693
2025-11-28 17:00 | 1764367200 | 1 | 0.2167 | 0.44 | 138.06 | 101.37 | 2.365
2025-11-28 18:00 | 1764370800 | 1 | 0.2222 | 0.45 | 135.47 | 100.32 | 2.32
2025-11-28 19:00 | 1764374400 | 1 | 0.2111 | 0.428 | 147.02 | 102.56 | 2.778
2025-11-28 20:00 | 1764378000 | 1 | 0.1472 | 0.297 | 144.27 | 97.93 | 2.014
2025-11-28 21:00 | 1764381600 | 1 | 0.2778 | 0.557 | 143.96 | 104.66 | 3.205
2025-11-28 22:00 | 1764385200 | 1 | 0.2583 | 0.525 | 143.82 | 109.41 | 2.639
2025-11-28 23:00 | 1764388800 | 1 | 0.3361 | 0.675 | 133.88 | 104.98 | 2.856
2025-11-29 00:00 | 1764392400 | 1 | 0.3472 | 0.695 | 143.85 | 113.73 | 3.068
2025-11-29 01:00 | 1764396000 | 1 | 0.4278 | 0.859 | 143.91 | 113.42 | 3.835
2025-11-29 02:00 | 1764399600 | 1 | 0.2889 | 0.577 | 145.67 | 111.67 | 2.875
2025-11-29 03:00 | 1764403200 | 1 | 0.2222 | 0.441 | 166.13 | 114.36 | 3.344
2025-11-29 04:00 | 1764406800 | 1 | 0.2111 | 0.425 | 163.19 | 108.75 | 3.379
2025-11-29 05:00 | 1764410400 | 1 | 0.2111 | 0.422 | 161.97 | 107.87 | 3.344
2025-11-29 06:00 | 1764414000 | 1 | 0.2111 | 0.424 | 160.56 | 108.16 | 3.242
2025-11-29 07:00 | 1764417600 | 1 | 0.2389 | 0.478 | 146.92 | 109.25 | 2.639
2025-11-29 08:00 | 1764421200 | 1 | 0.2333 | 0.466 | 149.66 | 107.5 | 2.88
2025-11-29 09:00 | 1764424800 | 1 | 0.2333 | 0.47 | 147.07 | 106.61 | 2.784
2025-11-29 10:00 | 1764428400 | 1 | 0.2111 | 0.428 | 145.33 | 102.38 | 2.693
2025-11-29 11:00 | 1764432000 | 1 | 0.2278 | 0.467 | 145.63 | 105.9 | 2.719
2025-11-29 12:00 | 1764435600 | 1 | 0.3583 | 0.721 | 136.65 | 104.71 | 3.37
2025-11-29 13:00 | 1764439200 | 1 | 0.2583 | 0.518 | 153.44 | 110.84 | 3.232
2025-11-29 14:00 | 1764442800 | 1 | 0.2278 | 0.456 | 150.79 | 108 | 2.856
2025-11-29 15:00 | 1764446400 | 1 | 0.2472 | 0.494 | 138.53 | 106.43 | 2.322
2025-11-29 16:00 | 1764450000 | 1 | 0.4139 | 0.83 | 141.13 | 108.62 | 3.955
2025-11-29 17:00 | 1764453600 | 1 | 0.2278 | 0.455 | 153.05 | 109.14 | 2.927
2025-11-29 18:00 | 1764457200 | 1 | 0.2389 | 0.475 | 140.29 | 106.19 | 2.376
2025-11-29 19:00 | 1764460800 | 1 | 0.2056 | 0.411 | 147.17 | 100.16 | 2.834
2025-11-29 20:00 | 1764464400 | 1 | 0.2 | 0.402 | 141.91 | 100.53 | 2.438
2025-11-29 21:00 | 1764468000 | 1 | 0.5389 | 1.08 | 144.21 | 116.24 | 4.425
2025-11-29 22:00 | 1764471600 | 1 | 0.7667 | 1.532 | 141.93 | 121.72 | 4.538
2025-11-29 23:00 | 1764475200 | 1 | 0.7444 | 1.489 | 147.43 | 125.41 | 4.802
2025-11-30 00:00 | 1764478800 | 1 | 0.6556 | 1.311 | 141.98 | 121.03 | 4.023
2025-11-30 01:00 | 1764482400 | 1 | 0.6528 | 1.312 | 146.23 | 121.5 | 4.748
2025-11-30 02:00 | 1764486000 | 1 | 0.4222 | 0.842 | 154.34 | 123.4 | 3.815
2025-11-30 03:00 | 1764489600 | 1 | 0.3417 | 0.681 | 169.81 | 121.14 | 4.851
2025-11-30 04:00 | 1764493200 | 1 | 0.3028 | 0.613 | 169.49 | 121.35 | 4.304
2025-11-30 05:00 | 1764496800 | 1 | 0.2556 | 0.507 | 165.66 | 118.34 | 3.517
2025-11-30 06:00 | 1764500400 | 1 | 0.2639 | 0.526 | 157.33 | 117.64 | 3.05
2025-11-30 07:00 | 1764504000 | 1 | 0.5 | 1 | 141.41 | 114.86 | 3.892
2025-11-30 08:00 | 1764507600 | 1 | 0.425 | 0.851 | 140.61 | 112.43 | 3.516
2025-11-30 09:00 | 1764511200 | 1 | 0.3333 | 0.674 | 164.76 | 121.51 | 4.259
2025-11-30 10:00 | 1764514800 | 1 | 0.375 | 0.75 | 166.25 | 120.48 | 5.033
2025-11-30 11:00 | 1764518400 | 1 | 0.1194 | 0.243 | 162.48 | 110.22 | 1.846
2025-11-30 19:00 | 1764547200 | 1 | 0.2306 | 0.46 | 134.72 | 105.6 | 1.963
2025-11-30 20:00 | 1764550800 | 1 | 0.4 | 0.798 | 133.87 | 107.13 | 3.126
2025-11-30 21:00 | 1764554400 | 1 | 0.3 | 0.602 | 141.55 | 113.74 | 2.443
2025-11-30 22:00 | 1764558000 | 1 | 0.4417 | 0.883 | 140.26 | 114.11 | 3.376
2025-11-30 23:00 | 1764561600 | 1 | 1 | 1.989 | 143.34 | 125.23 | 5.281
2025-12-01 00:00 | 1764565200 | 1 | 1 | 1.986 | 147.11 | 130.68 | 4.782
2025-12-01 01:00 | 1764568800 | 1 | 1 | 1.992 | 136.48 | 121.72 | 4.308
2025-12-01 02:00 | 1764572400 | 1 | 0.8139 | 1.617 | 138.99 | 121.82 | 4.069
2025-12-01 03:00 | 1764576000 | 1 | 0.6889 | 1.367 | 149.63 | 126.58 | 4.616
2025-12-01 04:00 | 1764579600 | 1 | 0.3722 | 0.745 | 143.87 | 118.08 | 2.81
2025-12-01 05:00 | 1764583200 | 1 | 0.5056 | 1.01 | 130.29 | 112.22 | 2.674
2025-12-01 06:00 | 1764586800 | 1 | 0.5833 | 1.162 | 141.22 | 118.99 | 3.787
2025-12-01 07:00 | 1764590400 | 1 | 0.325 | 0.646 | 140.61 | 115.83 | 2.347
2025-12-01 08:00 | 1764594000 | 1 | 0.1972 | 0.393 | 140.49 | 101.76 | 2.229
2025-12-01 09:00 | 1764597600 | 1 | 0.2028 | 0.407 | 144.98 | 104.04 | 2.443
2025-12-01 10:00 | 1764601200 | 1 | 0.2111 | 0.421 | 144.15 | 106.13 | 2.347
2025-12-01 11:00 | 1764604800 | 1 | 0.2111 | 0.419 | 140.69 | 103.81 | 2.263
2025-12-01 12:00 | 1764608400 | 1 | 0.3639 | 0.721 | 142.05 | 111.37 | 3.241
2025-12-01 13:00 | 1764612000 | 1 | 0.2667 | 0.528 | 156.85 | 117.44 | 3.046
2025-12-01 14:00 | 1764615600 | 1 | 0.2222 | 0.436 | 162.72 | 114.73 | 3.065
2025-12-01 15:00 | 1764619200 | 1 | 0.3361 | 0.666 | 150.61 | 115.44 | 3.432
2025-12-01 16:00 | 1764622800 | 1 | 0.1056 | 0.21 | 143.83 | 101.41 | 1.309
2025-12-01 17:00 | 1764626400 | 1 | 0.0944 | 0.198 | 137.45 | 93.43 | 1.268
2025-12-01 18:00 | 1764630000 | 1 | 0.5694 | 1.133 | 154.9 | 120.58 | 5.698
2025-12-01 19:00 | 1764633600 | 1 | 0.2611 | 0.519 | 158.86 | 121.26 | 2.861
2025-12-01 20:00 | 1764637200 | 1 | 0.4222 | 0.84 | 160.68 | 122.4 | 4.712
2025-12-01 21:00 | 1764640800 | 1 | 0.5389 | 1.08 | 155.71 | 124.5 | 4.934
2025-12-01 22:00 | 1764644400 | 1 | 0.5667 | 1.132 | 157.07 | 127.73 | 4.866
2025-12-01 23:00 | 1764648000 | 1 | 0.6528 | 1.271 | 156.03 | 128.36 | 5.148
2025-12-02 00:00 | 1764651600 | 1 | 0.5972 | 1.192 | 163.94 | 129.56 | 6.002
2025-12-02 01:00 | 1764655200 | 1 | 0.3694 | 0.735 | 166.26 | 126.14 | 4.319
2025-12-02 02:00 | 1764658800 | 1 | 0.5028 | 1.007 | 153.01 | 124.07 | 4.267
2025-12-02 03:00 | 1764662400 | 1 | 0.525 | 1.048 | 162.22 | 128.16 | 5.228
2025-12-02 04:00 | 1764666000 | 1 | 0.6056 | 1.212 | 153.07 | 124.53 | 5.068
2025-12-02 05:00 | 1764669600 | 1 | 0.5139 | 1.03 | 159.81 | 127.09 | 4.936
2025-12-02 06:00 | 1764673200 | 1 | 0.5361 | 1.076 | 150.79 | 125.15 | 4.039
2025-12-02 07:00 | 1764676800 | 1 | 0.5917 | 1.183 | 156.53 | 127.07 | 5.105
2025-12-02 08:00 | 1764680400 | 1 | 0.5028 | 1.007 | 164.28 | 126.56 | 5.569
2025-12-02 09:00 | 1764684000 | 1 | 0.3972 | 0.792 | 163.52 | 125.01 | 4.467
2025-12-02 10:00 | 1764687600 | 1 | 0.4583 | 0.913 | 162.32 | 127.37 | 4.676
2025-12-02 11:00 | 1764691200 | 1 | 0.4917 | 0.983 | 160.34 | 125.16 | 5.067
2025-12-02 12:00 | 1764694800 | 1 | 0.4861 | 0.97 | 159.6 | 124.86 | 4.936
2025-12-02 13:00 | 1764698400 | 1 | 0.4222 | 0.844 | 155.46 | 125.06 | 3.758
2025-12-02 14:00 | 1764702000 | 1 | 0.4167 | 0.832 | 160.22 | 122.19 | 4.636
2025-12-02 15:00 | 1764705600 | 1 | 0.2333 | 0.475 | 156.34 | 116.3 | 2.762
2025-12-02 16:00 | 1764709200 | 1 | 0.2111 | 0.423 | 139.52 | 101.71 | 2.346
2025-12-02 17:00 | 1764712800 | 1 | 0.2389 | 0.478 | 137.66 | 103.63 | 2.385
2025-12-02 18:00 | 1764716400 | 1 | 0.1889 | 0.379 | 162.98 | 103.79 | 3.283
2025-12-02 19:00 | 1764720000 | 1 | 0.35 | 0.698 | 161.17 | 119.7 | 4.243
2025-12-02 20:00 | 1764723600 | 1 | 0.7111 | 1.422 | 144.81 | 123.11 | 4.521
2025-12-02 21:00 | 1764727200 | 1 | 0.6833 | 1.369 | 158.43 | 129.36 | 5.827
2025-12-02 22:00 | 1764730800 | 1 | 0.4833 | 0.963 | 160.33 | 126.68 | 4.748
2025-12-02 23:00 | 1764734400 | 1 | 0.7139 | 1.43 | 135.37 | 118.53 | 3.528
2025-12-03 00:00 | 1764738000 | 0.9972 | 0.8969 | 1.797 | 146.99 | 125.15 | 5.736
2025-12-03 01:00 | 1764741600 | 1 | 0.675 | 1.347 | 155.58 | 131.16 | 4.82
2025-12-03 02:00 | 1764745200 | 1 | 0.65 | 1.303 | 136.58 | 117.04 | 3.73
2025-12-03 03:00 | 1764748800 | 1 | 0.7667 | 1.536 | 147.23 | 124.81 | 5.047
2025-12-03 04:00 | 1764752400 | 1 | 0.5222 | 1.044 | 159.28 | 127.7 | 4.832
2025-12-03 05:00 | 1764756000 | 1 | 0.1667 | 0.334 | 151.96 | 104.28 | 2.332
2025-12-03 06:00 | 1764759600 | 1 | 0.2944 | 0.594 | 140.05 | 105.95 | 2.966
2025-12-03 07:00 | 1764763200 | 1 | 0.3389 | 0.685 | 142.67 | 110.63 | 3.218
2025-12-03 08:00 | 1764766800 | 1 | 0.4806 | 0.96 | 162.51 | 126.43 | 5.077
2025-12-03 09:00 | 1764770400 | 1 | 0.4889 | 0.977 | 160.53 | 124.43 | 5.172
2025-12-03 10:00 | 1764774000 | 1 | 0.3056 | 0.611 | 158.63 | 121.83 | 3.295
2025-12-03 11:00 | 1764777600 | 1 | 0.4556 | 0.916 | 152.26 | 119.56 | 4.388
2025-12-03 12:00 | 1764781200 | 1 | 0.2722 | 0.544 | 150.34 | 115.48 | 2.782
2025-12-03 13:00 | 1764784800 | 1 | 0.35 | 0.702 | 148.45 | 111.35 | 3.813
2025-12-03 14:00 | 1764788400 | 1 | 0.3444 | 0.686 | 143.03 | 113.25 | 2.993
2025-12-03 15:00 | 1764792000 | 1 | 0.5278 | 1.058 | 144.62 | 117.9 | 4.144
2025-12-03 16:00 | 1764795600 | 1 | 0.4944 | 0.988 | 157.91 | 124.76 | 4.796
2025-12-03 17:00 | 1764799200 | 1 | 0.2389 | 0.48 | 154.29 | 114.3 | 2.813
2025-12-03 18:00 | 1764802800 | 1 | 0.1556 | 0.312 | 154.38 | 99.32 | 2.517
2025-12-03 19:00 | 1764806400 | 1 | 0.1667 | 0.333 | 156.34 | 107.02 | 2.409
2025-12-03 20:00 | 1764810000 | 1 | 0.1861 | 0.371 | 157.79 | 107.68 | 2.726
2025-12-03 21:00 | 1764813600 | 1 | 0.3417 | 0.685 | 146.43 | 109.6 | 3.697
2025-12-03 22:00 | 1764817200 | 1 | 0.3583 | 0.716 | 148.65 | 118.42 | 3.173
2025-12-03 23:00 | 1764820800 | 1 | 0.4472 | 0.883 | 158.95 | 121.63 | 4.82
2025-12-04 00:00 | 1764824400 | 1 | 0.4028 | 0.738 | 154.98 | 118.65 | 3.928
2025-12-04 01:00 | 1764828000 | 1 | 0.3778 | 0.758 | 150.63 | 118.27 | 3.596
2025-12-04 02:00 | 1764831600 | 1 | 0.3861 | 0.771 | 162.96 | 121.02 | 4.74
2025-12-04 03:00 | 1764835200 | 1 | 0.2583 | 0.519 | 153.65 | 118.05 | 2.689
2025-12-04 04:00 | 1764838800 | 1 | 0.3806 | 0.764 | 158.32 | 117.8 | 4.538
2025-12-04 05:00 | 1764842400 | 1 | 0.3028 | 0.61 | 160.25 | 120.34 | 3.56
2025-12-04 06:00 | 1764846000 | 1 | 0.3694 | 0.737 | 140.89 | 113.85 | 2.92
2025-12-04 07:00 | 1764849600 | 1 | 0.4194 | 0.841 | 138.33 | 113.93 | 3.006
2025-12-04 08:00 | 1764853200 | 1 | 0.3028 | 0.603 | 167.17 | 117.84 | 4.361
2025-12-04 09:00 | 1764856800 | 1 | 0.2167 | 0.433 | 163.44 | 113.92 | 3.144
2025-12-04 10:00 | 1764860400 | 1 | 0.2167 | 0.432 | 162.74 | 112.19 | 3.203
2025-12-04 11:00 | 1764864000 | 1 | 0.3222 | 0.644 | 159.77 | 113.58 | 4.357
2025-12-04 12:00 | 1764867600 | 1 | 0.275 | 0.549 | 160.08 | 116.71 | 3.492
2025-12-04 13:00 | 1764871200 | 1 | 0.25 | 0.498 | 157.25 | 116.48 | 2.977
2025-12-04 14:00 | 1764874800 | 1 | 0.3806 | 0.762 | 150.75 | 115.04 | 3.987
2025-12-04 15:00 | 1764878400 | 1 | 0.2972 | 0.599 | 154.57 | 118.03 | 3.199
2025-12-04 16:00 | 1764882000 | 1 | 0.3972 | 0.787 | 161.54 | 120.7 | 4.712
2025-12-04 17:00 | 1764885600 | 1 | 0.2194 | 0.439 | 164.68 | 122.01 | 2.745
2025-12-04 18:00 | 1764889200 | 1 | 0.2972 | 0.591 | 167.38 | 119.43 | 4.154
2025-12-04 19:00 | 1764892800 | 1 | 0.3972 | 0.798 | 163.52 | 125.02 | 4.499
2025-12-04 20:00 | 1764896400 | 1 | 0.5361 | 1.101 | 153.39 | 115.91 | 6.045
2025-12-04 22:00 | 1764903600 | 1 | 0.6028 | 1.308 | 149.39 | 120.43 | 5.551
2025-12-04 23:00 | 1764907200 | 1 | 0.6611 | 1.426 | 145.16 | 117.39 | 5.798
2025-12-05 00:00 | 1764910800 | 1 | 0.9 | 1.886 | 163.92 | 134.05 | 8.253
2025-12-05 01:00 | 1764914400 | 1 | 1 | 1.996 | 151.37 | 131.03 | 5.948
2025-12-05 02:00 | 1764918000 | 1 | 0.9194 | 1.827 | 166.93 | 141.24 | 6.878
2025-12-05 03:00 | 1764921600 | 1 | 0.8167 | 1.619 | 172.9 | 142.51 | 7.209
2025-12-05 04:00 | 1764925200 | 1 | 0.8028 | 1.597 | 155.35 | 131.78 | 5.518
2025-12-05 05:00 | 1764928800 | 1 | 1 | 1.983 | 161.27 | 136.74 | 7.129
2025-12-05 06:00 | 1764932400 | 1 | 0.9861 | 1.952 | 163.59 | 140.84 | 6.509
2025-12-05 07:00 | 1764936000 | 1 | 0.9 | 1.878 | 159.74 | 131.72 | 7.709
2025-12-05 08:00 | 1764939600 | 1 | 0.7556 | 1.497 | 169.37 | 138.09 | 6.861
2025-12-05 09:00 | 1764943200 | 1 | 0.5972 | 1.185 | 166.76 | 135.62 | 5.409
2025-12-05 10:00 | 1764946800 | 1 | 0.5611 | 1.117 | 161.63 | 128.02 | 5.503
2025-12-05 11:00 | 1764950400 | 1 | 0.3694 | 0.753 | 149.71 | 115.6 | 3.754
2025-12-05 12:00 | 1764954000 | 1 | 0.7417 | 1.58 | 135.33 | 112.58 | 5.27
2025-12-05 13:00 | 1764957600 | 1 | 0.5528 | 1.102 | 161.37 | 130.07 | 5.053
2025-12-05 14:00 | 1764961200 | 1 | 0.625 | 1.25 | 158.43 | 128.07 | 5.561
2025-12-05 15:00 | 1764964800 | 1 | 0.6278 | 1.247 | 156.7 | 128.3 | 5.189
2025-12-05 16:00 | 1764968400 | 1 | 0.7278 | 1.452 | 157.72 | 129.18 | 6.072
2025-12-05 17:00 | 1764972000 | 1 | 0.5861 | 1.324 | 154.5 | 122.86 | 6.135
2025-12-05 18:00 | 1764975600 | 1 | 0.7583 | 1.57 | 152.43 | 122.2 | 6.953
2025-12-05 19:00 | 1764979200 | 1 | 0.875 | 1.751 | 132.25 | 117.64 | 3.747
2025-12-05 20:00 | 1764982800 | 1 | 1 | 2.103 | 128.68 | 113.12 | 4.795
2025-12-05 21:00 | 1764986400 | 1 | 1 | 2.098 | 136.3 | 116.81 | 5.991
2025-12-05 22:00 | 1764990000 | 1 | 1 | 1.984 | 166.78 | 140.34 | 7.688
2025-12-05 23:00 | 1764993600 | 1 | 0.6194 | 1.314 | 167.85 | 134.07 | 6.503
2025-12-06 00:00 | 1764997200 | 1 | 0.6139 | 1.228 | 148.62 | 122.79 | 4.646
2025-12-06 01:00 | 1765000800 | 1 | 0.7556 | 1.614 | 138.2 | 116.46 | 5.144
2025-12-06 02:00 | 1765004400 | 1 | 0.5944 | 1.188 | 162.76 | 130.2 | 5.668
2025-12-06 03:00 | 1765008000 | 1 | 0.4306 | 0.905 | 164.48 | 125.27 | 5.195
2025-12-06 04:00 | 1765011600 | 1 | 0.6056 | 1.209 | 150.32 | 122.13 | 4.994
2025-12-06 05:00 | 1765015200 | 1 | 0.6333 | 1.223 | 164.87 | 127.95 | 6.614
2025-12-06 06:00 | 1765018800 | 1 | 0.475 | 0.947 | 168.48 | 133.01 | 4.921
2025-12-06 07:00 | 1765022400 | 1 | 0.6056 | 1.241 | 156.39 | 122.76 | 6.117
2025-12-06 08:00 | 1765026000 | 1 | 0.6056 | 1.207 | 151.98 | 123.88 | 4.97
2025-12-06 09:00 | 1765029600 | 1 | 0.5528 | 1.129 | 160.07 | 128.64 | 5.197
2025-12-06 10:00 | 1765033200 | 1 | 0.4722 | 0.94 | 154.88 | 115.33 | 5.449
2025-12-06 11:00 | 1765036800 | 1 | 0.2583 | 0.517 | 153.67 | 114.36 | 2.977
2025-12-06 12:00 | 1765040400 | 1 | 0.0861 | 0.128 | 146.6 | 87.4 | 1.112
2025-12-06 13:00 | 1765044000 | 1 | 0.1722 | 0.348 | 149.16 | 94.76 | 2.776
2025-12-06 14:00 | 1765047600 | 1 | 0.1944 | 0.492 | 142.72 | 95.03 | 3.437
2025-12-06 15:00 | 1765051200 | 1 | 0.3889 | 0.775 | 157.71 | 121.11 | 4.155
2025-12-06 16:00 | 1765054800 | 1 | 0.4556 | 0.909 | 157.87 | 122.6 | 4.699
2025-12-06 17:00 | 1765058400 | 1 | 0.4139 | 0.799 | 154.5 | 111.18 | 5.078
2025-12-06 18:00 | 1765062000 | 1 | 0.2389 | 0.481 | 156.79 | 110.03 | 3.288
2025-12-06 19:00 | 1765065600 | 1 | 0.1278 | 0.254 | 147.18 | 102.36 | 1.671
2025-12-06 20:00 | 1765069200 | 1 | 0.4083 | 0.813 | 152.41 | 116.02 | 4.335
2025-12-06 21:00 | 1765072800 | 1 | 0.3667 | 0.697 | 151.02 | 111.09 | 4.079
2025-12-06 22:00 | 1765076400 | 1 | 0.3722 | 0.747 | 152.43 | 115.29 | 4.063
2025-12-06 23:00 | 1765080000 | 1 | 0.5944 | 1.286 | 146.1 | 117.77 | 5.339
2025-12-07 00:00 | 1765083600 | 1 | 0.7528 | 1.509 | 136.5 | 118.18 | 4.052
2025-12-07 01:00 | 1765087200 | 1 | 0.7917 | 1.582 | 142.91 | 122.14 | 4.816
2025-12-07 02:00 | 1765090800 | 1 | 0.7639 | 1.62 | 145.84 | 122.77 | 5.476
2025-12-07 03:00 | 1765094400 | 1 | 0.7472 | 1.496 | 143.23 | 121.5 | 4.763
2025-12-07 04:00 | 1765098000 | 1 | 0.5194 | 1.134 | 167.17 | 125.74 | 6.876
2025-12-07 05:00 | 1765101600 | 1 | 0.3278 | 0.659 | 160.88 | 119.49 | 3.991
2025-12-07 06:00 | 1765105200 | 1 | 0.3833 | 0.768 | 153.57 | 120.54 | 3.707
2025-12-07 07:00 | 1765108800 | 1 | 0.5306 | 1.172 | 150.52 | 118.36 | 5.506
2025-12-07 08:00 | 1765112400 | 1 | 0.5 | 1 | 163.67 | 126.83 | 5.401
2025-12-07 09:00 | 1765116000 | 1 | 0.2833 | 0.61 | 158.85 | 113.14 | 4.078
2025-12-07 10:00 | 1765119600 | 1 | 0.2167 | 0.439 | 153.95 | 106.44 | 3.055
2025-12-07 11:00 | 1765123200 | 1 | 0.2 | 0.403 | 137.53 | 99.89 | 2.223
2025-12-07 12:00 | 1765126800 | 1 | 0.25 | 0.6 | 138.75 | 101.98 | 3.229
2025-12-07 13:00 | 1765130400 | 1 | 0.2278 | 0.458 | 152.79 | 107.22 | 3.059
2025-12-07 14:00 | 1765134000 | 1 | 0.2722 | 0.549 | 154.71 | 106.31 | 3.891
2025-12-07 15:00 | 1765137600 | 1 | 0.325 | 0.736 | 152.57 | 107.82 | 4.822
2025-12-07 16:00 | 1765141200 | 1 | 0.2389 | 0.482 | 149.99 | 108.78 | 2.9
2025-12-07 17:00 | 1765144800 | 1 | 0.2167 | 0.434 | 155.95 | 106.71 | 3.132
2025-12-07 18:00 | 1765148400 | 1 | 0.275 | 0.511 | 146.42 | 98.75 | 3.568
2025-12-07 19:00 | 1765152000 | 1 | 0.1556 | 0.311 | 154.79 | 100.12 | 2.49
2025-12-07 20:00 | 1765155600 | 1 | 0.2917 | 0.648 | 156 | 105.94 | 4.751
2025-12-07 21:00 | 1765159200 | 1 | 0.2111 | 0.424 | 152.48 | 105.96 | 2.885
2025-12-07 22:00 | 1765162800 | 1 | 0.2167 | 0.435 | 150.22 | 106.56 | 2.778
2025-12-07 23:00 | 1765166400 | 1 | 0.4806 | 0.929 | 153.79 | 113.78 | 5.446
2025-12-08 00:00 | 1765170000 | 1 | 0.6417 | 1.284 | 141.08 | 120.01 | 3.964
2025-12-08 01:00 | 1765173600 | 1 | 0.7889 | 1.673 | 145.25 | 121.8 | 5.748
2025-12-08 02:00 | 1765177200 | 1 | 0.6944 | 1.386 | 165.09 | 133.97 | 6.318
2025-12-08 03:00 | 1765180800 | 1 | 0.4806 | 0.958 | 157.82 | 126.61 | 4.381
2025-12-08 04:00 | 1765184400 | 1 | 0.6583 | 1.333 | 145.85 | 119.87 | 5.075
2025-12-08 05:00 | 1765188000 | 1 | 0.5083 | 1.012 | 168.92 | 130.25 | 5.733
2025-12-08 06:00 | 1765191600 | 1 | 0.3694 | 0.737 | 162.38 | 122.99 | 4.253
2025-12-08 07:00 | 1765195200 | 1 | 0.45 | 0.998 | 152.66 | 117.93 | 5.081
2025-12-08 08:00 | 1765198800 | 1 | 0.7 | 1.402 | 139.6 | 118.4 | 4.354
2025-12-08 09:00 | 1765202400 | 1 | 0.7472 | 1.491 | 155.25 | 125.97 | 6.398
2025-12-08 10:00 | 1765206000 | 1 | 0.3611 | 0.721 | 162.48 | 127.19 | 3.726
2025-12-08 11:00 | 1765209600 | 1 | 0.2889 | 0.541 | 159.42 | 105.76 | 4.25
2025-12-08 12:00 | 1765213200 | 1 | 0.2444 | 0.492 | 155.18 | 110.04 | 3.254
2025-12-08 14:00 | 1765220400 | 1 | 0.5667 | 1.185 | 163.9 | 126.03 | 6.575
2025-12-08 15:00 | 1765224000 | 1 | 0.5333 | 1.068 | 161.78 | 127.5 | 5.365
2025-12-08 16:00 | 1765227600 | 1 | 0.4639 | 0.926 | 169.1 | 133.19 | 4.868
2025-12-08 17:00 | 1765231200 | 1 | 0.6361 | 1.23 | 166.01 | 127.65 | 6.913
2025-12-08 18:00 | 1765234800 | 1 | 0.6333 | 1.27 | 161.06 | 129.53 | 5.87
2025-12-08 19:00 | 1765238400 | 1 | 0.6444 | 1.355 | 158.04 | 127.14 | 6.135
2025-12-08 20:00 | 1765242000 | 1 | 0.8556 | 1.706 | 152.57 | 129.54 | 5.757
2025-12-08 21:00 | 1765245600 | 1 | 0.7 | 1.391 | 167.66 | 135.85 | 6.484
2025-12-08 22:00 | 1765249200 | 1 | 0.4 | 0.839 | 160.81 | 123.03 | 4.645
2025-12-08 23:00 | 1765252800 | 1 | 0.6639 | 1.324 | 168.71 | 133.56 | 6.819
2025-12-09 00:00 | 1765256400 | 1 | 0.6833 | 1.332 | 159.07 | 127.27 | 6.206
2025-12-09 01:00 | 1765260000 | 1 | 0.7278 | 1.448 | 171.27 | 138.61 | 6.93
2025-12-09 02:00 | 1765263600 | 1 | 0.5806 | 1.195 | 158.33 | 128.3 | 5.256
2025-12-09 03:00 | 1765267200 | 1 | 0.8972 | 1.792 | 157.71 | 132.13 | 6.718
2025-12-09 04:00 | 1765270800 | 1 | 0.6194 | 1.325 | 167.93 | 134 | 6.585
2025-12-09 05:00 | 1765274400 | 1 | 0.7333 | 1.488 | 160.33 | 131.4 | 6.307
2025-12-09 06:00 | 1765278000 | 1 | 0.8 | 1.619 | 165.59 | 133.63 | 7.575
2025-12-09 07:00 | 1765281600 | 1 | 0.6722 | 1.338 | 168.87 | 138.43 | 5.967
2025-12-09 08:00 | 1765285200 | 1 | 0.6583 | 1.354 | 156.3 | 124.87 | 6.235
2025-12-09 09:00 | 1765288800 | 1 | 0.5667 | 1.179 | 164.67 | 130.91 | 5.835
2025-12-09 10:00 | 1765292400 | 1 | 0.475 | 0.955 | 160.99 | 124.07 | 5.164
2025-12-09 11:00 | 1765296000 | 1 | 0.2722 | 0.585 | 159.07 | 106.01 | 4.538
2025-12-09 12:00 | 1765299600 | 1 | 0.2472 | 0.494 | 149.98 | 112.74 | 2.696
2025-12-09 13:00 | 1765303200 | 1 | 0.4028 | 0.809 | 154.77 | 117.12 | 4.462
2025-12-09 14:00 | 1765306800 | 1 | 0.4583 | 0.974 | 148.82 | 115.33 | 4.78
2025-12-09 15:00 | 1765310400 | 1 | 0.5611 | 1.123 | 156.89 | 126.83 | 4.947
2025-12-09 16:00 | 1765314000 | 1 | 0.5833 | 1.164 | 165.8 | 131.46 | 5.857
2025-12-09 17:00 | 1765317600 | 1 | 0.525 | 1.032 | 170.86 | 128.16 | 6.46
2025-12-09 18:00 | 1765321200 | 1 | 0.4028 | 0.809 | 165.46 | 124.79 | 4.811
2025-12-09 19:00 | 1765324800 | 1 | 0.4194 | 0.931 | 163.85 | 122.87 | 5.589
2025-12-09 20:00 | 1765328400 | 1 | 0.5167 | 1.038 | 161.7 | 126.72 | 5.322
2025-12-09 21:00 | 1765332000 | 1 | 0.4278 | 0.854 | 159.36 | 122.38 | 4.628
2025-12-09 22:00 | 1765335600 | 1 | 0.3333 | 0.645 | 161.97 | 116.31 | 4.317
2025-12-09 23:00 | 1765339200 | 1 | 0.525 | 1.055 | 167.97 | 129.65 | 5.918
2025-12-10 00:00 | 1765342800 | 0.9972 | 0.5515 | 1.089 | 162.78 | 124.49 | 6.102
2025-12-10 01:00 | 1765346400 | 1 | 0.5056 | 1.013 | 159.05 | 126.81 | 4.78
2025-12-10 02:00 | 1765350000 | 1 | 0.7333 | 1.552 | 148.68 | 122.79 | 5.89
2025-12-10 03:00 | 1765353600 | 1 | 0.5306 | 1.066 | 167.23 | 133.3 | 5.29
2025-12-10 04:00 | 1765357200 | 1 | 0.55 | 1.098 | 153.64 | 125.61 | 4.508
2025-12-10 05:00 | 1765360800 | 1 | 0.5417 | 1.177 | 163.49 | 124.41 | 6.74
2025-12-10 06:00 | 1765364400 | 1 | 0.4861 | 0.974 | 144.85 | 117.81 | 3.86
2025-12-10 07:00 | 1765368000 | 1 | 0.6111 | 1.101 | 153.34 | 124.16 | 4.706
2025-12-10 08:00 | 1765371600 | 1 | 0.4667 | 0.929 | 168.99 | 124.15 | 6.12
2025-12-10 09:00 | 1765375200 | 1 | 0.2611 | 0.523 | 166.36 | 120.28 | 3.53
2025-12-10 10:00 | 1765378800 | 1 | 0.3167 | 0.634 | 163.93 | 115.07 | 4.542
2025-12-10 11:00 | 1765382400 | 1 | 0.2944 | 0.63 | 162.81 | 114.95 | 4.42
2025-12-10 12:00 | 1765386000 | 1 | 0.2472 | 0.5 | 162.34 | 117.68 | 3.259
2025-12-10 13:00 | 1765389600 | 1 | 0.4333 | 0.867 | 152.73 | 118.86 | 4.302
2025-12-10 14:00 | 1765393200 | 1 | 0.5028 | 1.103 | 133.4 | 109.98 | 3.785
2025-12-10 15:00 | 1765396800 | 1 | 0.55 | 1.108 | 148.72 | 120.91 | 4.513
2025-12-10 16:00 | 1765400400 | 1 | 0.2778 | 0.556 | 154.1 | 118.22 | 2.922
2025-12-10 17:00 | 1765404000 | 1 | 0.0889 | 0.178 | 149.38 | 96.17 | 1.39
2025-12-10 18:00 | 1765407600 | 1 | 0.2806 | 0.563 | 154.37 | 106.7 | 3.933
2025-12-10 19:00 | 1765411200 | 1 | 0.375 | 0.75 | 157.25 | 120.19 | 4.073
2025-12-10 20:00 | 1765414800 | 1 | 0.5167 | 1.037 | 146 | 117.49 | 4.331
2025-12-10 21:00 | 1765418400 | 1 | 0.4028 | 0.83 | 159.04 | 119.17 | 4.842
2025-12-10 22:00 | 1765422000 | 1 | 0.3111 | 0.621 | 149.09 | 113.27 | 3.26
2025-12-10 23:00 | 1765425600 | 1 | 0.3056 | 0.611 | 153.67 | 117.61 | 3.23
2025-12-11 00:00 | 1765429200 | 1 | 0.3889 | 0.777 | 155.16 | 118.41 | 4.184
2025-12-11 01:00 | 1765432800 | 1 | 0.4833 | 1.003 | 140.07 | 113.13 | 3.959
2025-12-11 02:00 | 1765436400 | 1 | 0.4056 | 0.815 | 151.07 | 118.51 | 3.885
2025-12-11 03:00 | 1765440000 | 1 | 0.3389 | 0.679 | 149.9 | 118.85 | 3.088
2025-12-11 04:00 | 1765443600 | 1 | 0.4556 | 1.008 | 141.14 | 112.29 | 4.257
2025-12-11 05:00 | 1765447200 | 1 | 0.5167 | 1.037 | 145.86 | 117.67 | 4.284
2025-12-11 06:00 | 1765450800 | 1 | 0.4083 | 0.901 | 149.08 | 113.75 | 4.659
2025-12-11 07:00 | 1765454400 | 1 | 0.2722 | 0.546 | 162.37 | 119.93 | 3.392
2025-12-11 08:00 | 1765458000 | 1 | 0.2111 | 0.431 | 159.86 | 109.94 | 3.145
2025-12-11 09:00 | 1765461600 | 1 | 0.2278 | 0.459 | 158.84 | 110.65 | 3.232
2025-12-11 10:00 | 1765465200 | 1 | 0.3167 | 0.635 | 157.41 | 111.99 | 4.227
2025-12-11 11:00 | 1765468800 | 1 | 0.2778 | 0.629 | 156.08 | 108.54 | 4.379
2025-12-11 12:00 | 1765472400 | 1 | 0.2333 | 0.468 | 154.78 | 112.91 | 2.871
2025-12-11 13:00 | 1765476000 | 1 | 0.2111 | 0.424 | 156 | 110.38 | 2.837
2025-12-11 14:00 | 1765479600 | 0.95 | 0.3275 | 0.659 | 153.26 | 102.98 | 4.609
2025-12-11 15:00 | 1765483200 | 1 | 0.2 | 0.446 | 167.5 | 103.31 | 4.2
2025-12-11 16:00 | 1765486800 | 1 | 0.2056 | 0.422 | 162.64 | 106.05 | 3.482
2025-12-11 17:00 | 1765490400 | 1 | 0.2333 | 0.473 | 161.3 | 114.49 | 3.235
2025-12-11 18:00 | 1765494000 | 1 | 0.3333 | 0.687 | 160.41 | 116.98 | 4.366
2025-12-11 19:00 | 1765497600 | 1 | 0.3278 | 0.676 | 160.94 | 119.12 | 4.141
2025-12-11 20:00 | 1765501200 | 1 | 0.3361 | 0.635 | 160.02 | 109.9 | 4.664
2025-12-11 21:00 | 1765504800 | 1 | 0.3778 | 0.762 | 162.78 | 122.86 | 4.452
2025-12-11 22:00 | 1765508400 | 1 | 0.4139 | 0.831 | 166.23 | 125.1 | 5
2025-12-11 23:00 | 1765512000 | 1 | 0.3611 | 0.723 | 165.78 | 122.93 | 4.536
2025-12-12 00:00 | 1765515600 | 1 | 0.375 | 0.771 | 171.15 | 123.86 | 5.329
2025-12-12 01:00 | 1765519200 | 1 | 0.3889 | 0.78 | 160.5 | 120.58 | 4.563
2025-12-12 02:00 | 1765522800 | 1 | 0.2944 | 0.589 | 169.56 | 126.04 | 3.754
2025-12-12 03:00 | 1765526400 | 1 | 0.4667 | 0.942 | 156.17 | 121.73 | 4.748
2025-12-12 04:00 | 1765530000 | 1 | 0.4333 | 0.87 | 166.53 | 126.4 | 5.114
2025-12-12 05:00 | 1765533600 | 1 | 0.3278 | 0.689 | 156.77 | 119.05 | 3.81
2025-12-12 06:00 | 1765537200 | 1 | 0.5194 | 1.043 | 152.8 | 121.17 | 4.834
2025-12-12 07:00 | 1765540800 | 1 | 0.3611 | 0.719 | 164.63 | 121.94 | 4.495
2025-12-12 08:00 | 1765544400 | 1 | 0.3667 | 0.82 | 165.61 | 120.55 | 5.414
2025-12-12 09:00 | 1765548000 | 1 | 0.4278 | 0.856 | 164.01 | 123.56 | 5.075
2025-12-12 10:00 | 1765551600 | 1 | 0.3778 | 0.755 | 161.29 | 121.12 | 4.443
2025-12-12 11:00 | 1765555200 | 1 | 0.4472 | 0.891 | 161.61 | 122.28 | 5.137
2025-12-12 12:00 | 1765558800 | 1 | 0.5972 | 1.195 | 153.22 | 124.05 | 5.11
2025-12-12 13:00 | 1765562400 | 1 | 0.5028 | 1.006 | 164.23 | 128.66 | 5.24
2025-12-12 14:00 | 1765566000 | 1 | 0.3528 | 0.77 | 156.27 | 115.63 | 4.57
2025-12-12 15:00 | 1765569600 | 1 | 0.55 | 1.108 | 145.34 | 120.42 | 4.047
2025-12-12 16:00 | 1765573200 | 1 | 0.5667 | 1.144 | 157.46 | 127.07 | 5.083
2025-12-12 17:00 | 1765576800 | 1 | 0.2556 | 0.52 | 157.22 | 115.46 | 3.175
2025-12-12 18:00 | 1765580400 | 1 | 0.2167 | 0.439 | 163.68 | 107.27 | 3.613
2025-12-12 19:00 | 1765584000 | 1 | 0.2167 | 0.432 | 162.48 | 109.01 | 3.387
2025-12-12 20:00 | 1765587600 | 1 | 0.2611 | 0.523 | 144.24 | 111.18 | 2.532
2025-12-12 21:00 | 1765591200 | 1 | 0.5889 | 1.181 | 160.04 | 124.65 | 6.119
2025-12-12 22:00 | 1765594800 | 1 | 0.5028 | 1.005 | 152.34 | 121.74 | 4.508
2025-12-12 23:00 | 1765598400 | 1 | 0.525 | 1.052 | 159.27 | 127.49 | 4.899
2025-12-13 00:00 | 1765602000 | 1 | 0.5917 | 1.072 | 152.85 | 123.19 | 4.659
2025-12-13 01:00 | 1765605600 | 1 | 0.575 | 1.154 | 158.54 | 126.04 | 5.488
2025-12-13 02:00 | 1765609200 | 1 | 0.4833 | 0.967 | 154.53 | 122.15 | 4.587
2025-12-13 03:00 | 1765612800 | 1 | 0.4083 | 0.816 | 164.86 | 129 | 4.285
2025-12-13 04:00 | 1765616400 | 1 | 0.5639 | 1.218 | 146.63 | 116.21 | 5.43
2025-12-13 05:00 | 1765620000 | 1 | 0.5361 | 1.076 | 164.64 | 128.46 | 5.7
2025-12-13 06:00 | 1765623600 | 1 | 0.3139 | 0.625 | 157.16 | 121.4 | 3.276
2025-12-13 07:00 | 1765627200 | 1 | 0.4611 | 0.931 | 152.42 | 119.59 | 4.481
2025-12-13 08:00 | 1765630800 | 1 | 0.4139 | 0.827 | 144.73 | 115.55 | 3.536
2025-12-13 09:00 | 1765634400 | 1 | 0.4306 | 0.846 | 153.23 | 118.73 | 4.273
2025-12-13 10:00 | 1765638000 | 1 | 0.3306 | 0.658 | 158.38 | 121.43 | 3.56
2025-12-13 11:00 | 1765641600 | 1 | 0.2389 | 0.475 | 147.31 | 113.02 | 2.389
2025-12-13 12:00 | 1765645200 | 1 | 0.4222 | 0.843 | 155.58 | 119.84 | 4.416
2025-12-13 13:00 | 1765648800 | 1 | 0.2917 | 0.583 | 154.35 | 118.37 | 3.076
2025-12-13 14:00 | 1765652400 | 1 | 0.3833 | 0.768 | 152.64 | 119.57 | 3.712
2025-12-13 15:00 | 1765656000 | 1 | 0.4611 | 0.919 | 147.28 | 118.25 | 3.912
2025-12-13 16:00 | 1765659600 | 1 | 0.4583 | 0.912 | 157.91 | 123.45 | 4.607
2025-12-13 17:00 | 1765663200 | 1 | 0.4111 | 0.82 | 149.16 | 119.92 | 3.511
2025-12-13 18:00 | 1765666800 | 1 | 0.4139 | 0.821 | 161.58 | 127.23 | 4.131
2025-12-13 19:00 | 1765670400 | 1 | 0.4639 | 0.926 | 161.13 | 126.13 | 4.741
2025-12-13 20:00 | 1765674000 | 1 | 0.4389 | 0.875 | 152.23 | 120.12 | 4.119
2025-12-13 21:00 | 1765677600 | 1 | 0.3167 | 0.628 | 164.33 | 126.79 | 3.457
2025-12-13 22:00 | 1765681200 | 1 | 0.4194 | 0.852 | 156.98 | 120.58 | 4.54
2025-12-13 23:00 | 1765684800 | 1 | 0.3528 | 0.706 | 159.55 | 122.15 | 3.868
2025-12-14 00:00 | 1765688400 | 1 | 0.4694 | 0.91 | 147.14 | 115.77 | 4.177
2025-12-14 01:00 | 1765692000 | 1 | 0.6167 | 1.231 | 152.44 | 123.81 | 5.166
2025-12-14 02:00 | 1765695600 | 1 | 0.3889 | 0.772 | 166.24 | 126.9 | 4.451
2025-12-14 03:00 | 1765699200 | 1 | 0.3278 | 0.653 | 155.87 | 123.39 | 3.108
2025-12-14 04:00 | 1765702800 | 1 | 0.5861 | 1.176 | 145.65 | 120.56 | 4.31
2025-12-14 05:00 | 1765706400 | 1 | 0.5306 | 1.059 | 166.11 | 131.07 | 5.436
2025-12-14 06:00 | 1765710000 | 1 | 0.4111 | 0.839 | 157.87 | 120.58 | 4.591
2025-12-14 07:00 | 1765713600 | 1 | 0.775 | 1.543 | 149.53 | 125.83 | 5.357
2025-12-14 08:00 | 1765717200 | 1 | 0.7583 | 1.503 | 169.69 | 140.87 | 6.346
2025-12-14 09:00 | 1765720800 | 1 | 0.625 | 1.241 | 157.56 | 132.06 | 4.631
2025-12-14 10:00 | 1765724400 | 1 | 0.7583 | 1.513 | 140.8 | 120.45 | 4.51
2025-12-14 11:00 | 1765728000 | 1 | 0.4444 | 0.887 | 156.84 | 123.35 | 4.354
2025-12-14 12:00 | 1765731600 | 1 | 0.4611 | 0.919 | 149.52 | 122.68 | 3.614
2025-12-14 13:00 | 1765735200 | 1 | 0.475 | 0.949 | 143.11 | 118.19 | 3.467
2025-12-14 14:00 | 1765738800 | 1 | 0.2917 | 0.582 | 138.73 | 108.63 | 2.566
2025-12-14 15:00 | 1765742400 | 1 | 0.3806 | 0.759 | 157.39 | 121.25 | 4.019
2025-12-14 16:00 | 1765746000 | 1 | 0.5417 | 1.078 | 154.21 | 125.06 | 4.605
2025-12-14 17:00 | 1765749600 | 1 | 0.6389 | 1.271 | 163.4 | 133.6 | 5.552
2025-12-14 18:00 | 1765753200 | 1 | 0.6083 | 1.204 | 160.47 | 132.29 | 4.972
2025-12-14 19:00 | 1765756800 | 1 | 1 | 1.989 | 139.3 | 123.57 | 4.584
2025-12-14 20:00 | 1765760400 | 1 | 0.775 | 1.536 | 165.26 | 137.18 | 6.319
2025-12-14 21:00 | 1765764000 | 1 | 0.7528 | 1.487 | 162.29 | 137.1 | 5.487
2025-12-14 22:00 | 1765767600 | 1 | 0.8944 | 1.778 | 153.02 | 131.24 | 5.672
2025-12-14 23:00 | 1765771200 | 1 | 0.7611 | 1.506 | 163.11 | 138.07 | 5.525
2025-12-15 00:00 | 1765774800 | 1 | 0.8944 | 1.776 | 149.12 | 130.52 | 4.84
2025-12-15 01:00 | 1765778400 | 1 | 0.7444 | 1.479 | 165.97 | 137.96 | 6.063
2025-12-15 02:00 | 1765782000 | 1 | 0.8722 | 1.732 | 147.77 | 130.02 | 4.506
2025-12-15 03:00 | 1765785600 | 1 | 1 | 1.99 | 150.25 | 130.04 | 5.893
2025-12-15 04:00 | 1765789200 | 1 | 0.7806 | 1.546 | 168.88 | 141.59 | 6.182
2025-12-15 05:00 | 1765792800 | 1 | 0.7611 | 1.515 | 149.44 | 130.19 | 4.273
2025-12-15 06:00 | 1765796400 | 1 | 0.8861 | 1.764 | 148.18 | 126.88 | 5.506
2025-12-15 07:00 | 1765800000 | 1 | 0.8972 | 1.783 | 155.43 | 133.01 | 5.858
2025-12-15 08:00 | 1765803600 | 1 | 0.7778 | 1.53 | 171.84 | 143.24 | 6.412
2025-12-15 09:00 | 1765807200 | 1 | 0.8917 | 1.761 | 165.75 | 140.49 | 6.517
2025-12-15 10:00 | 1765810800 | 1 | 0.7611 | 1.509 | 161.52 | 136.12 | 5.617
2025-12-15 11:00 | 1765814400 | 1 | 0.7083 | 1.412 | 142.62 | 123.76 | 3.902
2025-12-15 12:00 | 1765818000 | 1 | 0.7833 | 1.556 | 147.02 | 125.03 | 5.013
2025-12-15 13:00 | 1765821600 | 1 | 0.7556 | 1.499 | 160.52 | 135.75 | 5.442
2025-12-15 14:00 | 1765825200 | 1 | 0.8861 | 1.759 | 148.86 | 129.14 | 5.081
2025-12-15 15:00 | 1765828800 | 1 | 0.9111 | 1.802 | 166.06 | 141.22 | 6.559
2025-12-15 16:00 | 1765832400 | 1 | 1 | 1.985 | 150.52 | 131.66 | 5.486
2025-12-15 17:00 | 1765836000 | 1 | 1 | 1.968 | 166.76 | 142.01 | 7.136
2025-12-15 18:00 | 1765839600 | 1 | 1 | 1.972 | 164.52 | 141.76 | 6.574
2025-12-15 19:00 | 1765843200 | 1 | 0.5556 | 1.1 | 155.58 | 130.37 | 4.062
2025-12-15 20:00 | 1765846800 | 1 | 0.3639 | 0.726 | 154.64 | 116.61 | 4.043
2025-12-15 21:00 | 1765850400 | 1 | 0.4167 | 0.829 | 168.45 | 130.95 | 4.554
2025-12-15 22:00 | 1765854000 | 1 | 0.6417 | 1.272 | 160.46 | 131.97 | 5.306
2025-12-15 23:00 | 1765857600 | 1 | 0.6306 | 1.255 | 165.33 | 133.19 | 5.904
2025-12-16 00:00 | 1765861200 | 1 | 0.4944 | 0.979 | 170.33 | 138.01 | 4.637
2025-12-16 01:00 | 1765864800 | 1 | 0.6944 | 1.379 | 148.37 | 126.36 | 4.448
2025-12-16 02:00 | 1765868400 | 1 | 0.8972 | 1.789 | 150.91 | 126.85 | 6.307
2025-12-16 03:00 | 1765872000 | 1 | 0.7361 | 1.471 | 170.41 | 139.45 | 6.669
2025-12-16 04:00 | 1765875600 | 1 | 0.5722 | 1.139 | 159.98 | 131.06 | 4.829
2025-12-16 05:00 | 1765879200 | 1 | 1 | 1.999 | 143.54 | 124.43 | 5.598
2025-12-16 06:00 | 1765882800 | 1 | 0.775 | 1.543 | 169.51 | 139.05 | 6.887
2025-12-16 07:00 | 1765886400 | 1 | 0.5194 | 1.033 | 166 | 134.49 | 4.766
2025-12-16 08:00 | 1765890000 | 1 | 0.5333 | 1.065 | 152.39 | 120.63 | 4.954
2025-12-16 09:00 | 1765893600 | 1 | 0.4861 | 0.971 | 164.81 | 127.13 | 5.361
2025-12-16 10:00 | 1765897200 | 1 | 0.3083 | 0.619 | 163.44 | 125.07 | 3.48
2025-12-16 11:00 | 1765900800 | 1 | 0.2167 | 0.447 | 160.43 | 111.18 | 3.202
2025-12-16 12:00 | 1765904400 | 1 | 0.2361 | 0.481 | 157.43 | 110.3 | 3.303
2025-12-16 13:00 | 1765908000 | 1 | 0.2889 | 0.583 | 154.9 | 109.69 | 3.843
2025-12-16 14:00 | 1765911600 | 1 | 0.4111 | 0.824 | 142.83 | 114.85 | 3.38
2025-12-16 15:00 | 1765915200 | 1 | 0.4694 | 0.943 | 161.05 | 125.42 | 4.921
2025-12-16 16:00 | 1765918800 | 1 | 0.4139 | 0.83 | 160.56 | 120.66 | 4.851
2025-12-16 17:00 | 1765922400 | 1 | 0.2694 | 0.539 | 167.29 | 121.84 | 3.587
2025-12-16 18:00 | 1765926000 | 1 | 0.2472 | 0.495 | 164.34 | 115.78 | 3.519
2025-12-16 19:00 | 1765929600 | 1 | 0.4139 | 0.835 | 161.15 | 122.39 | 4.726
2025-12-16 20:00 | 1765933200 | 1 | 0.375 | 0.753 | 161.42 | 120.55 | 4.502
2025-12-16 21:00 | 1765936800 | 1 | 0.2889 | 0.578 | 158.18 | 116.79 | 3.506
2025-12-16 22:00 | 1765940400 | 1 | 0.4611 | 0.931 | 143.01 | 118.55 | 3.331
2025-12-16 23:00 | 1765944000 | 1 | 0.7278 | 1.455 | 160.78 | 131.06 | 6.336
2025-12-17 00:00 | 1765947600 | 0.9972 | 0.4903 | 0.987 | 159.58 | 128.05 | 4.533
2025-12-17 01:00 | 1765951200 | 1 | 0.6889 | 1.38 | 143.67 | 121.43 | 4.5
2025-12-17 02:00 | 1765954800 | 1 | 0.5417 | 1.084 | 160.29 | 129.07 | 4.952
2025-12-17 03:00 | 1765958400 | 1 | 0.5306 | 1.064 | 146.64 | 121.71 | 3.886
2025-12-17 04:00 | 1765962000 | 1 | 0.5472 | 1.097 | 161.32 | 128.92 | 5.205
2025-12-17 05:00 | 1765965600 | 1 | 0.4417 | 0.881 | 162.85 | 125.43 | 4.83
2025-12-17 06:00 | 1765969200 | 1 | 0.325 | 0.655 | 152.36 | 120.99 | 3
2025-12-17 07:00 | 1765972800 | 1 | 0.3944 | 0.795 | 153.66 | 118.27 | 4.11
2025-12-17 08:00 | 1765976400 | 1 | 0.425 | 0.852 | 145.54 | 113.22 | 4.026
2025-12-17 09:00 | 1765980000 | 1 | 0.3306 | 0.658 | 162.67 | 125.14 | 3.618
2025-12-17 10:00 | 1765983600 | 1 | 0.2389 | 0.481 | 158.77 | 114.92 | 3.081
2025-12-17 11:00 | 1765987200 | 1 | 0.325 | 0.649 | 156.61 | 112.61 | 4.183
2025-12-17 12:00 | 1765990800 | 1 | 0.2917 | 0.586 | 154.89 | 117.31 | 3.226
2025-12-17 13:00 | 1765994400 | 1 | 0.3972 | 0.792 | 146.56 | 113.85 | 3.799
2025-12-17 14:00 | 1765998000 | 1 | 0.3139 | 0.627 | 152.94 | 118.43 | 3.171
2025-12-17 15:00 | 1766001600 | 1 | 0.8833 | 1.765 | 145.99 | 123.83 | 5.733
2025-12-17 16:00 | 1766005200 | 1 | 0.7222 | 1.438 | 152.82 | 128.7 | 5.081
2025-12-17 17:00 | 1766008800 | 1 | 0.4944 | 0.99 | 139.16 | 117.25 | 3.178
2025-12-17 18:00 | 1766012400 | 1 | 0.1972 | 0.4 | 144.52 | 99.2 | 2.642
2025-12-17 19:00 | 1766016000 | 1 | 0.2361 | 0.472 | 142.61 | 106.41 | 2.502
2025-12-17 20:00 | 1766019600 | 1 | 0.2083 | 0.419 | 145.27 | 102.25 | 2.642
2025-12-17 21:00 | 1766023200 | 1 | 0.2889 | 0.58 | 150.87 | 115.4 | 3.004
2025-12-17 22:00 | 1766026800 | 1 | 0.4806 | 0.962 | 146.31 | 116.3 | 4.227
2025-12-17 23:00 | 1766030400 | 1 | 0.3417 | 0.681 | 160.93 | 121.59 | 3.928
2025-12-18 00:00 | 1766034000 | 1 | 0.3333 | 0.661 | 156.45 | 118.86 | 3.639
2025-12-18 01:00 | 1766037600 | 1 | 0.2889 | 0.576 | 151.88 | 115.77 | 3.046
2025-12-18 02:00 | 1766041200 | 1 | 0.35 | 0.692 | 155.29 | 116.82 | 3.901
2025-12-18 03:00 | 1766044800 | 1 | 0.1278 | 0.254 | 148.89 | 100.84 | 1.79
2025-12-18 04:00 | 1766048400 | 1 | 0.1889 | 0.38 | 160.63 | 108.77 | 2.883
2025-12-18 05:00 | 1766052000 | 1 | 0.2278 | 0.46 | 155.41 | 109.62 | 3.064
2025-12-18 06:00 | 1766055600 | 1 | 0.3722 | 0.743 | 149.48 | 112.77 | 3.992
2025-12-18 07:00 | 1766059200 | 1 | 0.2111 | 0.418 | 160.72 | 110.22 | 3.091
2025-12-18 08:00 | 1766062800 | 1 | 0.2056 | 0.411 | 157.75 | 106.13 | 3.1
2025-12-18 09:00 | 1766066400 | 1 | 0.1944 | 0.386 | 154.84 | 104.05 | 2.871
2025-12-18 10:00 | 1766070000 | 1 | 0.1167 | 0.232 | 157.29 | 106.92 | 1.709
2025-12-18 11:00 | 1766073600 | 1 | 0.0833 | 0.166 | 153.3 | 92.19 | 1.485
2025-12-18 12:00 | 1766077200 | 0.9972 | 0.0195 | 0.039 | 116.84 | 89.6 | 0.156
2025-12-18 13:00 | 1766080800 | 1 | 0.1944 | 0.388 | 134.94 | 93.43 | 2.363
2025-12-18 14:00 | 1766084400 | 1 | 0.2278 | 0.454 | 135.19 | 99.92 | 2.345
2025-12-18 15:00 | 1766088000 | 1 | 0.2444 | 0.486 | 140.11 | 104.68 | 2.523
2025-12-18 16:00 | 1766091600 | 1 | 0.2111 | 0.418 | 146.28 | 103.53 | 2.616
2025-12-18 17:00 | 1766095200 | 1 | 0.3389 | 0.67 | 146.06 | 103.72 | 4.157
2025-12-18 18:00 | 1766098800 | 1 | 0.0889 | 0.176 | 149.39 | 96.11 | 1.376
2025-12-18 19:00 | 1766102400 | 1 | 0.1222 | 0.242 | 146.08 | 93.44 | 1.87
2025-12-18 20:00 | 1766106000 | 1 | 0.1556 | 0.311 | 148.1 | 93.81 | 2.47
2025-12-18 21:00 | 1766109600 | 1 | 0.2944 | 0.585 | 134.55 | 105.99 | 2.449
2025-12-18 22:00 | 1766113200 | 1 | 0.4167 | 0.833 | 149.28 | 114.92 | 4.191
2025-12-18 23:00 | 1766116800 | 1 | 0.4167 | 0.825 | 141.39 | 113.45 | 3.378
2025-12-19 00:00 | 1766120400 | 1 | 0.5222 | 1.04 | 127.98 | 109.01 | 2.891
2025-12-19 01:00 | 1766124000 | 1 | 0.5611 | 1.115 | 139.7 | 116.88 | 3.729
2025-12-19 02:00 | 1766127600 | 1 | 0.5 | 0.993 | 138.28 | 114.71 | 3.432
2025-12-19 03:00 | 1766131200 | 1 | 0.5556 | 1.113 | 132.36 | 110.17 | 3.614
2025-12-19 04:00 | 1766134800 | 1 | 0.3 | 0.593 | 143.28 | 114.55 | 2.496
2025-12-19 05:00 | 1766138400 | 1 | 0.3667 | 0.726 | 140.84 | 109.4 | 3.343
2025-12-19 06:00 | 1766142000 | 1 | 0.2833 | 0.56 | 130.06 | 105.54 | 2.014
2025-12-19 07:00 | 1766145600 | 1 | 0.3611 | 0.725 | 131.89 | 105.1 | 2.844
2025-12-19 08:00 | 1766149200 | 1 | 0.2222 | 0.441 | 136.43 | 102.88 | 2.168
2025-12-19 09:00 | 1766152800 | 1 | 0.25 | 0.498 | 134 | 100.22 | 2.464
2025-12-19 10:00 | 1766156400 | 1 | 0.3111 | 0.617 | 134.53 | 103.24 | 2.83
2025-12-19 11:00 | 1766160000 | 1 | 0.2333 | 0.462 | 132.57 | 103.28 | 1.984
2025-12-19 12:00 | 1766163600 | 1 | 0.2778 | 0.555 | 131.13 | 101.23 | 2.426
2025-12-19 13:00 | 1766167200 | 1 | 0.2722 | 0.538 | 130.7 | 100.36 | 2.391
2025-12-19 14:00 | 1766170800 | 1 | 0.0944 | 0.187 | 128.29 | 94.62 | 0.923
2025-12-19 15:00 | 1766174400 | 1 | 0.8056 | 1.597 | 121.99 | 106.01 | 3.739
2025-12-19 16:00 | 1766178000 | 1 | 0.8972 | 1.784 | 117.68 | 106.64 | 2.883
2025-12-19 17:00 | 1766181600 | 1 | 1 | 1.988 | 118.83 | 109.33 | 2.768
2025-12-19 18:00 | 1766185200 | 1 | 1 | 1.991 | 107.13 | 99.15 | 2.328
2025-12-19 19:00 | 1766188800 | 1 | 1 | 1.987 | 106.28 | 98.04 | 2.397
2025-12-19 20:00 | 1766192400 | 0.95 | 0.5058 | 1.006 | 115.54 | 101.67 | 1.943
2025-12-19 21:00 | 1766196000 | 1 | 0 | 0 |  |  | 0
2025-12-19 22:00 | 1766199600 | 1 | 0.1417 | 0.285 | 146.74 | 85.94 | 2.537
2025-12-19 23:00 | 1766203200 | 1 | 0.1444 | 0.292 | 148.73 | 100.52 | 2.06
2025-12-20 00:00 | 1766206800 | 1 | 0.2111 | 0.424 | 145.21 | 102.62 | 2.647
2025-12-20 01:00 | 1766210400 | 1 | 0.2333 | 0.467 | 157.28 | 111.51 | 3.134
2025-12-20 02:00 | 1766214000 | 1 | 0.2417 | 0.483 | 151.63 | 111.18 | 2.865
2025-12-20 03:00 | 1766217600 | 1 | 0.5 | 1.005 | 137.64 | 111.77 | 3.803
2025-12-20 04:00 | 1766221200 | 1 | 0.4917 | 0.985 | 157.11 | 124.15 | 4.756
2025-12-20 05:00 | 1766224800 | 1 | 0.4917 | 0.984 | 150.99 | 120.15 | 4.436
2025-12-20 06:00 | 1766228400 | 1 | 0.2917 | 0.588 | 159.69 | 121.21 | 3.306
2025-12-20 07:00 | 1766232000 | 1 | 0.4556 | 0.916 | 148.24 | 117.93 | 4.048
2025-12-20 08:00 | 1766235600 | 1 | 0.825 | 1.653 | 140.49 | 119.48 | 5.085
2025-12-20 09:00 | 1766239200 | 1 | 0.8972 | 1.792 | 147.02 | 126.55 | 5.377
2025-12-20 10:00 | 1766242800 | 1 | 0.7833 | 1.561 | 140.65 | 120.18 | 4.679
2025-12-20 11:00 | 1766246400 | 1 | 0.1 | 0.2 | 154.67 | 102.68 | 1.523
2025-12-20 12:00 | 1766250000 | 1 | 0.2056 | 0.417 | 152.11 | 100.79 | 3.117
2025-12-20 13:00 | 1766253600 | 1 | 0.2056 | 0.413 | 147.16 | 101.84 | 2.744
2025-12-20 14:00 | 1766257200 | 1 | 0.7889 | 1.575 | 155.36 | 128.9 | 6.106
2025-12-20 15:00 | 1766260800 | 1 | 0.7528 | 1.509 | 151.4 | 128.95 | 4.962
2025-12-20 16:00 | 1766264400 | 1 | 0.7444 | 1.493 | 135.42 | 116.45 | 4.149
2025-12-20 17:00 | 1766268000 | 1 | 0.2556 | 0.51 | 155.2 | 117.19 | 2.839
2025-12-20 18:00 | 1766271600 | 1 | 0.0833 | 0.172 | 149.51 | 91.53 | 1.436
2025-12-20 19:00 | 1766275200 | 1 | 0.2 | 0.41 | 148.67 | 98.9 | 2.984
2025-12-20 20:00 | 1766278800 | 1 | 0.2167 | 0.437 | 143.92 | 101.98 | 2.675
2025-12-20 22:00 | 1766286000 | 1 | 0.45 | 0.902 | 148.39 | 119.44 | 3.826
2025-12-20 23:00 | 1766289600 | 1 | 0.4889 | 0.983 | 154.64 | 123.41 | 4.488
2025-12-21 00:00 | 1766293200 | 1 | 0.5167 | 1.036 | 151.78 | 120.48 | 4.745
2025-12-21 01:00 | 1766296800 | 1 | 0.3667 | 0.733 | 155 | 119.35 | 3.831
2025-12-21 02:00 | 1766300400 | 1 | 0.3778 | 0.754 | 150.51 | 119.36 | 3.443
2025-12-21 03:00 | 1766304000 | 1 | 0.4444 | 0.894 | 154.4 | 119.37 | 4.588
2025-12-21 04:00 | 1766307600 | 1 | 0.3333 | 0.664 | 151.91 | 116.43 | 3.451
2025-12-21 05:00 | 1766311200 | 1 | 0.3833 | 0.766 | 145.3 | 117.52 | 3.116
2025-12-21 06:00 | 1766314800 | 1 | 0.4111 | 0.818 | 152.09 | 119.77 | 3.87
2025-12-21 07:00 | 1766318400 | 1 | 0.3389 | 0.673 | 143.21 | 114.01 | 2.88
2025-12-21 08:00 | 1766322000 | 1 | 0.3444 | 0.69 | 151.99 | 118.31 | 3.401
2025-12-21 09:00 | 1766325600 | 1 | 0.2111 | 0.424 | 149.46 | 108.68 | 2.521
2025-12-21 10:00 | 1766329200 | 1 | 0.2111 | 0.419 | 143.72 | 105.56 | 2.344
2025-12-21 11:00 | 1766332800 | 1 | 0.0889 | 0.176 | 145.41 | 97.27 | 1.243
2025-12-22 13:00 | 1766426400 | 1 | 1 | 2.097 | 140.03 | 119.72 | 6.243
2025-12-22 14:00 | 1766430000 | 1 | 1 | 1.984 | 155.5 | 134.44 | 6.122
2025-12-22 15:00 | 1766433600 | 1 | 0.9306 | 1.907 | 153.66 | 129.93 | 6.632
2025-12-22 16:00 | 1766437200 | 1 | 0.4889 | 0.973 | 162.29 | 128.06 | 4.878
2025-12-22 17:00 | 1766440800 | 1 | 0.8694 | 1.729 | 141.38 | 123.76 | 4.463
2025-12-22 18:00 | 1766444400 | 1 | 1 | 2.088 | 122.39 | 108.51 | 4.247
2025-12-22 19:00 | 1766448000 | 1 | 1 | 2.098 | 125.08 | 106.26 | 5.785
2025-12-22 20:00 | 1766451600 | 1 | 1 | 1.952 | 163.28 | 140.3 | 6.572
2025-12-22 21:00 | 1766455200 | 1 | 1 | 2.108 | 157.8 | 130.32 | 8.489
2025-12-22 22:00 | 1766458800 | 1 | 1 | 1.992 | 160.84 | 138.97 | 6.386
2025-12-22 23:00 | 1766462400 | 1 | 1 | 2.093 | 148.62 | 126.1 | 6.906
2025-12-23 00:00 | 1766466000 | 1 | 1 | 1.988 | 170.1 | 144.05 | 7.584
2025-12-23 01:00 | 1766469600 | 1 | 1 | 2.074 | 150.68 | 129.74 | 6.365
2025-12-23 02:00 | 1766473200 | 1 | 0.9167 | 1.83 | 161.52 | 135.72 | 6.918
2025-12-23 03:00 | 1766476800 | 1 | 0.5611 | 1.118 | 168.19 | 136.46 | 5.2
2025-12-23 04:00 | 1766480400 | 1 | 0.6889 | 1.433 | 152.32 | 124.29 | 5.88
2025-12-23 05:00 | 1766484000 | 1 | 0.4917 | 0.985 | 163.65 | 130.88 | 4.729
2025-12-23 06:00 | 1766487600 | 1 | 0.3167 | 0.614 | 164.33 | 111.9 | 4.701
2025-12-23 07:00 | 1766491200 | 1 | 0.1667 | 0.336 | 158.25 | 109.51 | 2.387
2025-12-23 08:00 | 1766494800 | 1 | 0.4361 | 0.86 | 174.32 | 118.23 | 7.057
2025-12-23 09:00 | 1766498400 | 1 | 0.3472 | 0.702 | 172.31 | 126.27 | 4.721
2025-12-23 10:00 | 1766502000 | 1 | 0.4278 | 0.859 | 170.25 | 129.98 | 5.061
2025-12-23 11:00 | 1766505600 | 1 | 0.2306 | 0.521 | 168.56 | 116.6 | 3.965
2025-12-23 12:00 | 1766509200 | 1 | 0.4389 | 0.918 | 145.85 | 119.38 | 3.561
2025-12-23 13:00 | 1766512800 | 1 | 0.4861 | 0.974 | 158.84 | 124.87 | 4.847
2025-12-23 14:00 | 1766516400 | 1 | 0.4528 | 0.909 | 146.34 | 120.02 | 3.507
2025-12-23 15:00 | 1766520000 | 1 | 0.5778 | 1.193 | 138.2 | 117.1 | 3.687
2025-12-23 16:00 | 1766523600 | 1 | 0.4306 | 0.93 | 161.36 | 118.94 | 5.767
2025-12-23 17:00 | 1766527200 | 1 | 0.1361 | 0.276 | 155.54 | 105.22 | 2.022
2025-12-23 18:00 | 1766530800 | 1 | 0.1639 | 0.332 | 159.62 | 105.63 | 2.623
2025-12-23 19:00 | 1766534400 | 1 | 0.3278 | 0.626 | 158.65 | 104.48 | 4.965
2025-12-23 20:00 | 1766538000 | 1 | 0.4556 | 0.919 | 145.23 | 118.3 | 3.624
2025-12-23 21:00 | 1766541600 | 1 | 0.5611 | 1.124 | 154.46 | 123.09 | 5.167
2025-12-23 22:00 | 1766545200 | 1 | 0.4583 | 0.954 | 151.9 | 118.9 | 4.611
2025-12-23 23:00 | 1766548800 | 1 | 0.6889 | 1.389 | 141.71 | 119.53 | 4.514
2025-12-24 00:00 | 1766552400 | 0.9972 | 0.5738 | 1.229 | 160.86 | 126.41 | 6.187
2025-12-24 01:00 | 1766556000 | 1 | 0.4583 | 0.919 | 160.36 | 128.64 | 4.273
2025-12-24 02:00 | 1766559600 | 1 | 0.7056 | 1.516 | 134 | 113.58 | 4.537
2025-12-24 03:00 | 1766563200 | 1 | 0.8944 | 1.796 | 143.65 | 123.66 | 5.261
2025-12-24 04:00 | 1766566800 | 1 | 0.7278 | 1.453 | 159.92 | 133.32 | 5.663
2025-12-24 05:00 | 1766570400 | 1 | 0.5639 | 1.223 | 144.71 | 119.15 | 4.576
2025-12-24 06:00 | 1766574000 | 1 | 0.8889 | 1.786 | 139.49 | 120.36 | 5.005
2025-12-24 07:00 | 1766577600 | 1 | 0.75 | 1.501 | 148.57 | 126.91 | 4.764
2025-12-24 08:00 | 1766581200 | 1 | 0.4361 | 0.872 | 171.83 | 129.94 | 5.351
2025-12-24 09:00 | 1766584800 | 1 | 0.325 | 0.746 | 167.11 | 116.93 | 5.485
2025-12-24 10:00 | 1766588400 | 1 | 0.2444 | 0.489 | 166.06 | 118.11 | 3.436
2025-12-24 11:00 | 1766592000 | 1 | 0.3139 | 0.623 | 163.56 | 115.78 | 4.365
2025-12-24 12:00 | 1766595600 | 1 | 0.3889 | 0.782 | 139.56 | 113.6 | 2.977
2025-12-24 13:00 | 1766599200 | 1 | 0.4944 | 0.991 | 161.87 | 124.65 | 5.404
2025-12-24 14:00 | 1766602800 | 1 | 0.4556 | 0.979 | 157.23 | 118.61 | 5.541
2025-12-24 15:00 | 1766606400 | 1 | 0.4972 | 0.999 | 138.66 | 116.64 | 3.223
2025-12-24 16:00 | 1766610000 | 1 | 0.6083 | 1.218 | 160.82 | 128.76 | 5.72
2025-12-24 19:00 | 1766620800 | 1 | 0.2278 | 0.455 | 166.75 | 116.86 | 3.32
2025-12-24 20:00 | 1766624400 | 1 | 0.2167 | 0.434 | 146.39 | 108.66 | 2.402
2025-12-24 21:00 | 1766628000 | 1 | 0.4056 | 0.815 | 145.17 | 111.79 | 3.987
2025-12-24 22:00 | 1766631600 | 1 | 0.5361 | 1.073 | 158.46 | 124.01 | 5.418
2025-12-24 23:00 | 1766635200 | 1 | 0.8556 | 1.714 | 146.52 | 125.72 | 5.226
2025-12-25 00:00 | 1766638800 | 1 | 0.8306 | 1.658 | 162.64 | 136.22 | 6.418
2025-12-25 01:00 | 1766642400 | 1 | 0.6528 | 1.308 | 167.33 | 135.36 | 6.122
2025-12-25 02:00 | 1766646000 | 1 | 0.6972 | 1.399 | 141.65 | 122.13 | 4.002
2025-12-25 03:00 | 1766649600 | 1 | 0.8917 | 1.788 | 147.93 | 125.79 | 5.804
2025-12-25 04:00 | 1766653200 | 1 | 0.5611 | 1.119 | 171.5 | 138.77 | 5.369
2025-12-25 05:00 | 1766656800 | 1 | 0.4667 | 0.937 | 168.95 | 129.57 | 5.4
2025-12-25 06:00 | 1766660400 | 1 | 0.5028 | 1.015 | 140.14 | 117.5 | 3.355
2025-12-25 07:00 | 1766664000 | 1 | 0.7139 | 1.426 | 158.95 | 129.89 | 6.074
2025-12-25 08:00 | 1766667600 | 1 | 0.4056 | 0.81 | 162.81 | 129.73 | 3.927
2025-12-25 09:00 | 1766671200 | 1 | 0.4417 | 0.889 | 160.88 | 122.93 | 4.944
2025-12-25 10:00 | 1766674800 | 1 | 0.325 | 0.652 | 159.57 | 118.65 | 3.9
2025-12-25 11:00 | 1766678400 | 1 | 0.3972 | 0.807 | 150.26 | 118.25 | 3.785
2025-12-25 12:00 | 1766682000 | 1 | 0.5167 | 1.035 | 140.96 | 116.05 | 3.778
2025-12-25 13:00 | 1766685600 | 1 | 0.5528 | 1.116 | 149.02 | 120.9 | 4.586
2025-12-25 14:00 | 1766689200 | 1 | 0.5417 | 1.085 | 149.76 | 124.13 | 4.075
2025-12-25 15:00 | 1766692800 | 1 | 0.6306 | 1.266 | 145.06 | 121.46 | 4.378
2025-12-25 16:00 | 1766696400 | 1 | 0.6028 | 1.209 | 144.9 | 120.82 | 4.268
2025-12-25 17:00 | 1766700000 | 1 | 0.6833 | 1.363 | 160.5 | 130.51 | 5.991
2025-12-25 18:00 | 1766703600 | 1 | 0.4083 | 0.822 | 159.39 | 123.56 | 4.313
2025-12-25 19:00 | 1766707200 | 1 | 0.4556 | 0.917 | 155.75 | 123.21 | 4.371
2025-12-25 20:00 | 1766710800 | 1 | 0.6861 | 1.373 | 155.94 | 128.85 | 5.45
2025-12-25 21:00 | 1766714400 | 1 | 0.7667 | 1.535 | 159.26 | 132.02 | 6.128
2025-12-25 22:00 | 1766718000 | 1 | 0.5611 | 1.119 | 169.21 | 135.07 | 5.599
2025-12-25 23:00 | 1766721600 | 1 | 0.65 | 1.298 | 154.8 | 129.95 | 4.726
2025-12-26 00:00 | 1766725200 | 1 | 0.7444 | 1.487 | 157.8 | 131.8 | 5.667
2025-12-26 01:00 | 1766728800 | 1 | 0.6556 | 1.309 | 170.98 | 137.4 | 6.44
2025-12-26 02:00 | 1766732400 | 1 | 0.7 | 1.4 | 146.56 | 126.45 | 4.124
2025-12-26 03:00 | 1766736000 | 1 | 1 | 2.002 | 147.87 | 127.44 | 5.994
2025-12-26 04:00 | 1766739600 | 1 | 0.7722 | 1.54 | 168.4 | 138.86 | 6.667
2025-12-26 05:00 | 1766743200 | 1 | 0.2917 | 0.668 | 166.38 | 117.64 | 4.769
2025-12-26 06:00 | 1766746800 | 1 | 0.4639 | 0.928 | 157.56 | 124.55 | 4.49
2025-12-26 07:00 | 1766750400 | 1 | 0.5972 | 1.192 | 168.46 | 131.19 | 6.508
2025-12-26 08:00 | 1766754000 | 1 | 0.4167 | 0.832 | 163.43 | 124.28 | 4.773
2025-12-26 09:00 | 1766757600 | 1 | 0.4167 | 0.834 | 163.04 | 125.6 | 4.576
2025-12-26 10:00 | 1766761200 | 1 | 0.4361 | 0.95 | 156.1 | 119.26 | 5.128
2025-12-26 11:00 | 1766764800 | 1 | 0.3889 | 0.778 | 152.24 | 114.66 | 4.283
2025-12-26 12:00 | 1766768400 | 1 | 0.3028 | 0.606 | 151.24 | 116.23 | 3.107
2025-12-26 13:00 | 1766772000 | 1 | 0.5028 | 1.014 | 143.6 | 116.07 | 4.079
2025-12-26 14:00 | 1766775600 | 1 | 0.5639 | 1.205 | 163.1 | 124.97 | 6.723
2025-12-26 15:00 | 1766779200 | 1 | 0.3944 | 0.787 | 165.26 | 124.61 | 4.69
2025-12-26 16:00 | 1766782800 | 1 | 0.4611 | 0.927 | 158.13 | 125.72 | 4.404
2025-12-26 17:00 | 1766786400 | 1 | 0.4972 | 0.994 | 165.78 | 129.47 | 5.282
2025-12-26 18:00 | 1766790000 | 1 | 0.6361 | 1.362 | 150.4 | 119.81 | 6.104
2025-12-26 19:00 | 1766793600 | 1 | 0.7556 | 1.524 | 149.66 | 125.76 | 5.335
2025-12-26 20:00 | 1766797200 | 1 | 0.8833 | 1.777 | 140.54 | 122.46 | 4.708
2025-12-26 21:00 | 1766800800 | 1 | 0.7778 | 1.635 | 145.84 | 122.2 | 5.661
2025-12-26 22:00 | 1766804400 | 1 | 1 | 2.003 | 163.51 | 137.28 | 7.697
2025-12-26 23:00 | 1766808000 | 1 | 0.9806 | 1.956 | 176.12 | 148 | 8.059
2025-12-27 00:00 | 1766811600 | 1 | 1 | 1.998 | 156.1 | 135.8 | 5.945
2025-12-27 01:00 | 1766815200 | 1 | 1 | 2.009 | 138.73 | 122.18 | 4.872
2025-12-27 02:00 | 1766818800 | 1 | 1 | 2 | 159.99 | 135.76 | 7.101
2025-12-27 03:00 | 1766822400 | 1 | 1 | 1.994 | 173.72 | 146.4 | 7.98
2025-12-27 04:00 | 1766826000 | 1 | 1 | 1.996 | 159.89 | 138.43 | 6.278
2025-12-27 05:00 | 1766829600 | 1 | 1 | 2.039 | 137.92 | 120.24 | 5.281
2025-12-27 06:00 | 1766833200 | 1 | 1 | 1.998 | 162.28 | 137.43 | 7.274
2025-12-27 07:00 | 1766836800 | 1 | 1 | 1.992 | 170.51 | 144.67 | 7.542
2025-12-27 08:00 | 1766840400 | 1 | 1 | 2.004 | 142.52 | 126.65 | 4.659
2025-12-27 09:00 | 1766844000 | 1 | 1 | 2.082 | 143.85 | 121.74 | 6.745
2025-12-27 10:00 | 1766847600 | 1 | 0.9389 | 1.872 | 169.31 | 142.27 | 7.418
2025-12-27 11:00 | 1766851200 | 1 | 0.7194 | 1.432 | 158.46 | 132.62 | 5.423
2025-12-27 12:00 | 1766854800 | 1 | 0.8861 | 1.78 | 135.29 | 117.61 | 4.613
2025-12-27 13:00 | 1766858400 | 1 | 0.8972 | 1.8 | 147.99 | 126.6 | 5.643
2025-12-27 14:00 | 1766862000 | 1 | 0.5278 | 1.057 | 162.32 | 130.23 | 4.97
2025-12-27 15:00 | 1766865600 | 1 | 0.325 | 0.65 | 157.24 | 116.14 | 3.916
2025-12-27 16:00 | 1766869200 | 1 | 0.7472 | 1.502 | 137.17 | 117.28 | 4.377
2025-12-27 17:00 | 1766872800 | 1 | 0.5972 | 1.194 | 152.51 | 125.44 | 4.729
2025-12-27 18:00 | 1766876400 | 1 | 0.2083 | 0.42 | 167.13 | 119.84 | 2.907
2025-12-27 19:00 | 1766880000 | 1 | 0.3417 | 0.683 | 162.37 | 114.75 | 4.767
2025-12-27 20:00 | 1766883600 | 1 | 0.1833 | 0.369 | 157.03 | 107.71 | 2.669
2025-12-27 21:00 | 1766887200 | 1 | 0.3361 | 0.676 | 135.98 | 108.17 | 2.756
2025-12-27 22:00 | 1766890800 | 1 | 0.5444 | 1.101 | 159.52 | 123.9 | 5.746
2025-12-27 23:00 | 1766894400 | 1 | 0.3861 | 0.814 | 167.78 | 118.57 | 5.866
2025-12-28 00:00 | 1766898000 | 1 | 0.4583 | 0.921 | 156.78 | 125.71 | 4.191
2025-12-28 01:00 | 1766901600 | 1 | 0.8222 | 1.648 | 151.67 | 127.17 | 5.916
2025-12-28 02:00 | 1766905200 | 1 | 0.6389 | 1.276 | 169.77 | 135.35 | 6.438
2025-12-28 03:00 | 1766908800 | 1 | 0.5028 | 1.004 | 164.94 | 133.83 | 4.573
2025-12-28 04:00 | 1766912400 | 1 | 0.9083 | 1.92 | 137.67 | 118.21 | 5.476
2025-12-28 05:00 | 1766916000 | 1 | 0.7 | 1.392 | 165.62 | 136.5 | 5.941
2025-12-28 06:00 | 1766919600 | 1 | 0.5306 | 1.057 | 170.51 | 136.04 | 5.336
2025-12-28 07:00 | 1766923200 | 1 | 0.5778 | 1.146 | 146.9 | 123.18 | 3.982
2025-12-28 08:00 | 1766926800 | 1 | 0.7778 | 1.659 | 143.77 | 120.17 | 5.74
2025-12-28 09:00 | 1766930400 | 1 | 0.575 | 1.145 | 165.85 | 132.38 | 5.611
2025-12-28 10:00 | 1766934000 | 1 | 0.2139 | 0.426 | 161.84 | 115.56 | 2.888
2025-12-28 11:00 | 1766937600 | 1 | 0.0944 | 0.194 | 158.09 | 101.08 | 1.598
2025-12-28 12:00 | 1766941200 | 1 | 0.0917 | 0.183 | 151.85 | 98.66 | 1.43
2025-12-28 13:00 | 1766944800 | 1 | 0.2917 | 0.592 | 130.06 | 95.14 | 3.032
2025-12-28 14:00 | 1766948400 | 1 | 0.5528 | 1.11 | 131.45 | 108.61 | 3.716
2025-12-28 15:00 | 1766952000 | 1 | 0.5 | 1.002 | 160.96 | 126.56 | 5.051
2025-12-28 16:00 | 1766955600 | 1 | 0.55 | 1.102 | 154.51 | 126.18 | 4.57
2025-12-28 17:00 | 1766959200 | 1 | 0.6222 | 1.244 | 140.75 | 119.94 | 3.792
2025-12-28 18:00 | 1766962800 | 1 | 0.4028 | 0.808 | 164.87 | 125.14 | 4.705
2025-12-28 19:00 | 1766966400 | 1 | 0.3556 | 0.708 | 160.72 | 123.68 | 3.843
2025-12-28 20:00 | 1766970000 | 1 | 0.7167 | 1.428 | 151.47 | 127.5 | 5.016
2025-12-28 21:00 | 1766973600 | 1 | 0.6278 | 1.248 | 158.84 | 132.95 | 4.734
2025-12-28 22:00 | 1766977200 | 1 | 0.6972 | 1.387 | 153.76 | 129.81 | 4.87
2025-12-28 23:00 | 1766980800 | 1 | 0.7556 | 1.515 | 154.17 | 128.39 | 5.721
2025-12-29 00:00 | 1766984400 | 1 | 0.5139 | 1.023 | 162.5 | 132.77 | 4.45
2025-12-29 01:00 | 1766988000 | 1 | 0.6278 | 1.256 | 145.75 | 125.09 | 3.802
2025-12-29 02:00 | 1766991600 | 1 | 0.8056 | 1.612 | 146.41 | 124.77 | 5.112
2025-12-29 03:00 | 1766995200 | 1 | 0.5806 | 1.156 | 164.87 | 133.87 | 5.251
2025-12-29 04:00 | 1766998800 | 1 | 0.4083 | 0.815 | 161.39 | 130.35 | 3.702
2025-12-29 05:00 | 1767002400 | 1 | 0.6917 | 1.38 | 142.36 | 120.43 | 4.434
2025-12-29 06:00 | 1767006000 | 1 | 0.7556 | 1.508 | 149.77 | 127.22 | 4.984
2025-12-29 07:00 | 1767009600 | 1 | 0.5306 | 1.061 | 161.93 | 131.4 | 4.743
2025-12-29 08:00 | 1767013200 | 1 | 0.5333 | 1.072 | 145.83 | 124.01 | 3.426
2025-12-29 09:00 | 1767016800 | 1 | 0.7278 | 1.45 | 149.44 | 124.8 | 5.237
2025-12-29 10:00 | 1767020400 | 1 | 0.5222 | 1.038 | 164.58 | 133.1 | 4.79
2025-12-29 11:00 | 1767024000 | 1 | 0.5 | 1.003 | 158.6 | 127.57 | 4.559
2025-12-29 12:00 | 1767027600 | 1 | 0.4778 | 0.954 | 156.22 | 125.71 | 4.26
2025-12-29 13:00 | 1767031200 | 1 | 0.5222 | 1.045 | 132.2 | 114.44 | 2.72
2025-12-29 14:00 | 1767034800 | 1 | 1 | 2.001 | 127.6 | 114.46 | 3.853
2025-12-29 15:00 | 1767038400 | 1 | 0.7861 | 1.572 | 149.2 | 128.21 | 4.833
2025-12-29 16:00 | 1767042000 | 1 | 0.6139 | 1.23 | 141.09 | 121.95 | 3.448
2025-12-29 17:00 | 1767045600 | 1 | 0.6333 | 1.271 | 127.31 | 112.5 | 2.756
2025-12-29 18:00 | 1767049200 | 1 | 0.4389 | 0.878 | 136.54 | 112.14 | 3.139
2025-12-29 19:00 | 1767052800 | 1 | 0.2056 | 0.417 | 133.11 | 102.28 | 1.875
2025-12-29 20:00 | 1767056400 | 1 | 0.2 | 0.404 | 133.18 | 100.86 | 1.906
2025-12-29 21:00 | 1767060000 | 1 | 0.2111 | 0.426 | 133.23 | 102.95 | 1.883
2025-12-29 22:00 | 1767063600 | 1 | 0.475 | 0.953 | 133.76 | 110.93 | 3.189
2025-12-29 23:00 | 1767067200 | 1 | 0.5139 | 1.029 | 139.22 | 116.34 | 3.45
2025-12-30 00:00 | 1767070800 | 1 | 0.3917 | 0.779 | 158.44 | 127.83 | 3.494
2025-12-30 01:00 | 1767074400 | 1 | 0.4194 | 0.836 | 149.47 | 119.93 | 3.619
2025-12-30 02:00 | 1767078000 | 1 | 0.5306 | 1.063 | 134.5 | 114.01 | 3.189
2025-12-30 03:00 | 1767081600 | 1 | 0.5528 | 1.104 | 143.72 | 121.32 | 3.625
2025-12-30 04:00 | 1767085200 | 1 | 0.4556 | 0.909 | 158.05 | 126.47 | 4.208
2025-12-30 05:00 | 1767088800 | 1 | 0.4194 | 0.839 | 150.12 | 119.72 | 3.739
2025-12-30 06:00 | 1767092400 | 1 | 0.5222 | 1.045 | 139.18 | 117.11 | 3.381
2025-12-30 07:00 | 1767096000 | 1 | 0.5528 | 1.109 | 148.74 | 125.67 | 3.747
2025-12-30 08:00 | 1767099600 | 1 | 0.5528 | 1.105 | 159.48 | 127.28 | 5.21
2025-12-30 09:00 | 1767103200 | 1 | 0.4056 | 0.812 | 164.79 | 126.31 | 4.576
2025-12-30 10:00 | 1767106800 | 1 | 0.3167 | 0.63 | 164.13 | 127.35 | 3.398
2025-12-30 11:00 | 1767110400 | 1 | 0.4806 | 0.954 | 157.63 | 125.85 | 4.445
2025-12-30 12:00 | 1767114000 | 1 | 0.6833 | 1.366 | 146.47 | 123.48 | 4.603
2025-12-30 13:00 | 1767117600 | 1 | 0.7222 | 1.436 | 165.52 | 137.43 | 5.911
2025-12-30 14:00 | 1767121200 | 1 | 0.5639 | 1.124 | 162.39 | 132.47 | 4.927
2025-12-30 15:00 | 1767124800 | 1 | 0.6778 | 1.345 | 157.09 | 132.28 | 4.889
2025-12-30 16:00 | 1767128400 | 1 | 0.6306 | 1.253 | 152.55 | 127.96 | 4.515
2025-12-30 17:00 | 1767132000 | 1 | 0.5472 | 1.1 | 134.8 | 114.67 | 3.243
2025-12-30 18:00 | 1767135600 | 1 | 0.4333 | 0.864 | 154.82 | 123.47 | 3.965
2025-12-30 19:00 | 1767139200 | 1 | 0.4056 | 0.816 | 148.98 | 117.01 | 3.816
2025-12-30 20:00 | 1767142800 | 1 | 0.5389 | 1.156 | 136.69 | 110.17 | 4.491
2025-12-30 21:00 | 1767146400 | 1 | 0.85 | 1.648 | 143.09 | 120.32 | 5.497
2025-12-30 22:00 | 1767150000 | 1 | 1 | 2.104 | 147.07 | 126.47 | 6.351
2025-12-30 23:00 | 1767153600 | 1 | 1 | 2.104 | 140.47 | 121.62 | 5.811
2025-12-31 00:00 | 1767157200 | 0.9972 | 1 | 2.089 | 160.46 | 135.19 | 7.714
2025-12-31 01:00 | 1767160800 | 1 | 1 | 2.087 | 155.32 | 133.87 | 6.562
2025-12-31 02:00 | 1767164400 | 1 | 1 | 1.988 | 148.46 | 129.21 | 5.608
2025-12-31 03:00 | 1767168000 | 1 | 1 | 2.096 | 143.79 | 125.43 | 5.638
2025-12-31 04:00 | 1767171600 | 1 | 1 | 2.096 | 155.84 | 133.57 | 6.842
2025-12-31 05:00 | 1767175200 | 1 | 1 | 2.091 | 145.47 | 126.6 | 5.78
2025-12-31 06:00 | 1767178800 | 1 | 1 | 2.103 | 135.6 | 118.49 | 5.273
2025-12-31 07:00 | 1767182400 | 1 | 1 | 2.092 | 150.97 | 129.65 | 6.535
2025-12-31 08:00 | 1767186000 | 1 | 1 | 2.037 | 143.52 | 124.54 | 5.666
2025-12-31 09:00 | 1767189600 | 1 | 0.9722 | 1.99 | 151.05 | 129.83 | 6.188
2025-12-31 10:00 | 1767193200 | 1 | 0.8972 | 1.888 | 148.66 | 125.56 | 6.392
2025-12-31 11:00 | 1767196800 | 1 | 0.4389 | 0.952 | 131.85 | 108.42 | 3.267
2025-12-31 12:00 | 1767200400 | 1 | 0.9444 | 1.983 | 141.35 | 120.01 | 6.2
2025-12-31 13:00 | 1767204000 | 1 | 1 | 1.981 | 170.07 | 144.28 | 7.487
2025-12-31 14:00 | 1767207600 | 1 | 0.7944 | 1.676 | 161.75 | 135.12 | 6.543
2025-12-31 15:00 | 1767211200 | 1 | 0.7222 | 1.436 | 163.45 | 136.75 | 5.621
2025-12-31 16:00 | 1767214800 | 1 | 0.5306 | 1.151 | 173.61 | 132.99 | 6.837
2025-12-31 17:00 | 1767218400 | 1 | 0.5667 | 1.126 | 156.02 | 128.1 | 4.606
2025-12-31 18:00 | 1767222000 | 1 | 0.7611 | 1.625 | 146.21 | 122.81 | 5.573
2025-12-31 19:00 | 1767225600 | 1 | 1 | 2.101 | 143.25 | 124.07 | 5.906
2025-12-31 20:00 | 1767229200 | 1 | 1 | 1.996 | 142.98 | 126.45 | 4.836
2025-12-31 21:00 | 1767232800 | 1 | 0.7278 | 1.543 | 162.65 | 131.18 | 7.116
2025-12-31 22:00 | 1767236400 | 1 | 0.3694 | 0.74 | 174.57 | 134.8 | 4.305
2025-12-31 23:00 | 1767240000 | 1 | 0.4889 | 0.943 | 172.32 | 125.89 | 6.419
2026-01-01 00:00 | 1767243600 | 1 | 0.4694 | 0.935 | 153.26 | 124.92 | 3.884
2026-01-01 01:00 | 1767247200 | 1 | 0.7583 | 1.606 | 157.35 | 129.48 | 6.561
2026-01-01 02:00 | 1767250800 | 1 | 0.475 | 1.045 | 173.94 | 133.99 | 6.107
2026-01-01 03:00 | 1767254400 | 1 | 0.4417 | 0.874 | 168.16 | 133.49 | 4.441
2026-01-01 04:00 | 1767258000 | 1 | 0.7111 | 1.518 | 144.86 | 119.87 | 5.553
2026-01-01 05:00 | 1767261600 | 1 | 0.6778 | 1.349 | 159.61 | 133.32 | 5.197
2026-01-01 06:00 | 1767265200 | 1 | 0.4861 | 1.043 | 173.18 | 130.55 | 6.508
2026-01-01 07:00 | 1767268800 | 1 | 0.2639 | 0.525 | 167.58 | 127.86 | 3.055
2026-01-01 08:00 | 1767272400 | 1 | 0.3472 | 0.654 | 146.47 | 105.58 | 3.916
2026-01-01 09:00 | 1767276000 | 1 | 0.3417 | 0.731 | 167.2 | 118.68 | 5.199
2026-01-01 10:00 | 1767279600 | 1 | 0.3194 | 0.638 | 162.83 | 121.57 | 3.851
2026-01-01 11:00 | 1767283200 | 1 | 0.6 | 1.189 | 137.53 | 115.27 | 3.876
2026-01-01 12:00 | 1767286800 | 1 | 0.6083 | 1.195 | 155.45 | 126.36 | 5.09
2026-01-01 13:00 | 1767290400 | 1 | 0.1861 | 0.325 | 166.14 | 104.94 | 2.895
2026-01-01 14:00 | 1767294000 | 1 | 0.2056 | 0.398 | 165.6 | 110.09 | 3.241
2026-01-01 15:00 | 1767297600 | 1 | 0.175 | 0.323 | 157.92 | 100.5 | 2.715
2026-01-01 16:00 | 1767301200 | 1 | 0.3139 | 0.624 | 135.13 | 105.2 | 2.735
2026-01-01 17:00 | 1767304800 | 1 | 0.8889 | 1.886 | 121 | 106.02 | 4.138
2026-01-01 18:00 | 1767308400 | 1 | 0.7778 | 1.647 | 152.18 | 126.18 | 6.275
2026-01-01 19:00 | 1767312000 | 1 | 0.4556 | 0.908 | 169.06 | 130.14 | 5.176
2026-01-01 20:00 | 1767315600 | 1 | 0.2806 | 0.607 | 171.53 | 116.86 | 4.862
2026-01-01 21:00 | 1767319200 | 1 | 0.3028 | 0.561 | 169.08 | 113.9 | 4.536
2026-01-01 22:00 | 1767322800 | 1 | 0.7694 | 1.628 | 135.96 | 114.4 | 5.144
2026-01-01 23:00 | 1767326400 | 1 | 1 | 2.097 | 155.22 | 130.87 | 7.484
2026-01-02 00:00 | 1767330000 | 1 | 0.9028 | 1.908 | 165.32 | 138.2 | 7.582
2026-01-02 01:00 | 1767333600 | 1 | 0.7694 | 1.582 | 171.06 | 141.57 | 6.836
2026-01-02 02:00 | 1767337200 | 1 | 0.75 | 1.544 | 163.96 | 136.01 | 6.322
2026-01-02 03:00 | 1767340800 | 1 | 0.8861 | 1.875 | 162.37 | 134.74 | 7.593
2026-01-02 04:00 | 1767344400 | 1 | 0.7694 | 1.594 | 166.19 | 135.52 | 7.162
2026-01-02 05:00 | 1767348000 | 1 | 0.7722 | 1.615 | 165.51 | 136.24 | 6.924
2026-01-02 06:00 | 1767351600 | 1 | 0.7528 | 1.587 | 165.46 | 135.01 | 7.079
2026-01-02 07:00 | 1767355200 | 1 | 0.7639 | 1.62 | 160.61 | 132.51 | 6.672
2026-01-02 08:00 | 1767358800 | 1 | 0.8278 | 1.618 | 169.13 | 136.96 | 7.628
2026-01-02 09:00 | 1767362400 | 1 | 0.775 | 1.545 | 158.28 | 134.04 | 5.488
2026-01-02 10:00 | 1767366000 | 1 | 0.8972 | 1.898 | 150.99 | 127.8 | 6.45
2026-01-02 11:00 | 1767369600 | 1 | 0.7028 | 1.519 | 138.44 | 116.85 | 4.804
2026-01-02 12:00 | 1767373200 | 1 | 0.8167 | 1.741 | 143.79 | 120.43 | 5.96
2026-01-02 13:00 | 1767376800 | 1 | 0.7444 | 1.571 | 160.61 | 129.52 | 7.155
2026-01-02 14:00 | 1767380400 | 1 | 0.5167 | 1.136 | 172.46 | 132.77 | 6.608
2026-01-02 15:00 | 1767384000 | 1 | 0.7 | 1.499 | 160.12 | 131.6 | 6.266
2026-01-02 16:00 | 1767387600 | 1 | 0.8861 | 1.764 | 154.76 | 133.03 | 5.616
2026-01-02 17:00 | 1767391200 | 1 | 0.7611 | 1.628 | 147.24 | 123.63 | 5.632
2026-01-02 18:00 | 1767394800 | 1 | 0.5389 | 1.153 | 144.22 | 116.17 | 4.739
2026-01-02 19:00 | 1767398400 | 1 | 0.7861 | 1.689 | 135.94 | 116.55 | 4.798
2026-01-02 20:00 | 1767402000 | 1 | 0.8917 | 1.882 | 142.57 | 120.33 | 6.135
2026-01-02 21:00 | 1767405600 | 1 | 0.75 | 1.501 | 163.25 | 134.79 | 6.259
2026-01-02 22:00 | 1767409200 | 1 | 0.6 | 1.291 | 166.89 | 134.07 | 6.205
2026-01-02 23:00 | 1767412800 | 1 | 0.7222 | 1.488 | 164.54 | 134.33 | 6.589
2026-01-03 00:00 | 1767416400 | 1 | 0.7306 | 1.51 | 166.57 | 136.26 | 6.705
2026-01-03 01:00 | 1767420000 | 1 | 0.6722 | 1.449 | 163.34 | 132.46 | 6.558
2026-01-03 02:00 | 1767423600 | 1 | 0.65 | 1.387 | 164.37 | 132.74 | 6.427
2026-01-03 03:00 | 1767427200 | 1 | 0.7083 | 1.425 | 168.86 | 138.09 | 6.425
2026-01-03 04:00 | 1767430800 | 1 | 0.6556 | 1.268 | 166.79 | 133.11 | 6.254
2026-01-03 05:00 | 1767434400 | 1 | 0.7444 | 1.58 | 164.42 | 133.02 | 7.271
2026-01-03 06:00 | 1767438000 | 1 | 0.5944 | 1.187 | 164.93 | 135.33 | 5.149
2026-01-03 07:00 | 1767441600 | 1 | 0.9611 | 1.892 | 157.31 | 131.1 | 7.268
2026-01-03 08:00 | 1767445200 | 1 | 0.7778 | 1.649 | 166.89 | 136.87 | 7.253
2026-01-03 09:00 | 1767448800 | 1 | 0.7556 | 1.501 | 166.72 | 139.33 | 6.025
2026-01-03 10:00 | 1767452400 | 1 | 0.7083 | 1.517 | 161.4 | 132.86 | 6.345
2026-01-03 11:00 | 1767456000 | 1 | 0.425 | 0.911 | 173.69 | 124.69 | 6.545
2026-01-03 12:00 | 1767459600 | 1 | 0.2722 | 0.541 | 169.63 | 125.65 | 3.481
2026-01-03 13:00 | 1767463200 | 1 | 0.7556 | 1.474 | 146.85 | 119.75 | 5.856
2026-01-03 14:00 | 1767466800 | 1 | 0.8917 | 1.878 | 157.74 | 131.62 | 7.188
2026-01-03 15:00 | 1767470400 | 1 | 0.7778 | 1.642 | 168.61 | 138.72 | 7.195
2026-01-03 16:00 | 1767474000 | 1 | 0.7611 | 1.515 | 168.76 | 139.97 | 6.39
2026-01-03 17:00 | 1767477600 | 1 | 0.7556 | 1.612 | 163.94 | 133.26 | 7.25
2026-01-03 18:00 | 1767481200 | 1 | 0.7389 | 1.573 | 165.53 | 135.15 | 7.001
2026-01-03 19:00 | 1767484800 | 1 | 0.7389 | 1.471 | 165.56 | 137.24 | 6.106
2026-01-03 20:00 | 1767488400 | 1 | 0.5194 | 1.064 | 159.72 | 125.1 | 5.398
2026-01-03 21:00 | 1767492000 | 1 | 0.4611 | 0.902 | 162.78 | 123.35 | 5.211
2026-01-03 22:00 | 1767495600 | 1 | 0.65 | 1.327 | 162.73 | 131.13 | 6.142
2026-01-03 23:00 | 1767499200 | 1 | 0.6361 | 1.332 | 165.4 | 132.27 | 6.469
2026-01-04 00:00 | 1767502800 | 1 | 0.7333 | 1.561 | 167.24 | 134.77 | 7.426
2026-01-04 01:00 | 1767506400 | 1 | 0.7 | 1.396 | 168.24 | 139.02 | 5.977
2026-01-04 02:00 | 1767510000 | 1 | 0.7333 | 1.423 | 165.79 | 134.42 | 6.544
2026-01-04 03:00 | 1767513600 | 1 | 0.7278 | 1.56 | 166.68 | 134 | 7.47
2026-01-04 04:00 | 1767517200 | 1 | 0.6778 | 1.35 | 170.97 | 140.06 | 6.112
2026-01-04 05:00 | 1767520800 | 1 | 0.6972 | 1.493 | 164.16 | 133.62 | 6.678
2026-01-04 06:00 | 1767524400 | 1 | 0.7861 | 1.66 | 166.39 | 135.69 | 7.467
2026-01-04 07:00 | 1767528000 | 1 | 0.7444 | 1.486 | 166.03 | 138.26 | 6.049
2026-01-04 08:00 | 1767531600 | 1 | 0.825 | 1.754 | 163.89 | 134.41 | 7.577
2026-01-04 09:00 | 1767535200 | 1 | 0.6194 | 1.337 | 163.97 | 132.73 | 6.121
2026-01-04 10:00 | 1767538800 | 1 | 0.5722 | 1.15 | 169.97 | 135.71 | 5.766
2026-01-04 11:00 | 1767542400 | 1 | 0.2889 | 0.546 | 167.24 | 112.64 | 4.366
2026-01-04 12:00 | 1767546000 | 1 | 0.3556 | 0.711 | 160.84 | 119.81 | 4.266
2026-01-04 13:00 | 1767549600 | 1 | 0.825 | 1.61 | 138.6 | 118.09 | 4.839
2026-01-04 14:00 | 1767553200 | 1 | 0.8972 | 1.889 | 162.99 | 133.64 | 8.123
2026-01-04 15:00 | 1767556800 | 1 | 0.6639 | 1.308 | 173.97 | 142.38 | 6.055
2026-01-04 16:00 | 1767560400 | 1 | 0.7139 | 1.466 | 164.05 | 132.33 | 6.813
2026-01-04 17:00 | 1767564000 | 1 | 0.8861 | 1.761 | 156.29 | 133.59 | 5.858
2026-01-04 18:00 | 1767567600 | 1 | 0.6806 | 1.452 | 168.5 | 133.58 | 7.424
2026-01-04 19:00 | 1767571200 | 1 | 0.2917 | 0.592 | 172.21 | 128.18 | 3.809
2026-01-04 20:00 | 1767574800 | 1 | 0.4278 | 0.814 | 172.86 | 121.76 | 6.093
2026-01-04 21:00 | 1767578400 | 1 | 0.2417 | 0.467 | 155.4 | 111.55 | 2.991
2026-01-04 22:00 | 1767582000 | 1 | 0.775 | 1.6 | 150.35 | 124.74 | 6.004
2026-01-04 23:00 | 1767585600 | 1 | 0.8528 | 1.802 | 169.33 | 137.74 | 8.343
2026-01-05 00:00 | 1767589200 | 1 | 0.7472 | 1.596 | 158.91 | 131.65 | 6.375
2026-01-05 01:00 | 1767592800 | 1 | 0.8639 | 1.72 | 167.41 | 140.35 | 6.821
2026-01-05 02:00 | 1767596400 | 1 | 0.7944 | 1.562 | 166 | 135.56 | 6.967
2026-01-05 03:00 | 1767600000 | 1 | 0.825 | 1.602 | 164.27 | 134.16 | 7.072
2026-01-05 04:00 | 1767603600 | 1 | 0.7056 | 1.405 | 166.42 | 138.77 | 5.693
2026-01-05 05:00 | 1767607200 | 1 | 0.975 | 2.055 | 143.66 | 123.93 | 5.944
2026-01-05 06:00 | 1767610800 | 1 | 1 | 2.101 | 147.71 | 125.76 | 6.757
2026-01-05 07:00 | 1767614400 | 1 | 1 | 2.098 | 156.51 | 132.99 | 7.229
2026-01-05 08:00 | 1767618000 | 1 | 1 | 2.099 | 151.2 | 128.99 | 6.831
2026-01-05 09:00 | 1767621600 | 1 | 1 | 2 | 144.84 | 127.08 | 5.204
2026-01-05 10:00 | 1767625200 | 1 | 1 | 2.106 | 136.1 | 118.61 | 5.398
2026-01-05 11:00 | 1767628800 | 1 | 1 | 2.115 | 134.56 | 117.5 | 5.286
2026-01-05 12:00 | 1767632400 | 1 | 1 | 2.11 | 132.67 | 116.28 | 5.067
2026-01-05 13:00 | 1767636000 | 1 | 1 | 1.994 | 159.95 | 135.44 | 7.163
2026-01-05 14:00 | 1767639600 | 1 | 1 | 2.068 | 169.46 | 142.67 | 8.119
2026-01-05 15:00 | 1767643200 | 1 | 0.8722 | 1.791 | 160.61 | 134.73 | 6.79
2026-01-05 16:00 | 1767646800 | 1 | 0.7361 | 1.505 | 166.15 | 136.15 | 6.616
2026-01-05 17:00 | 1767650400 | 1 | 0.8028 | 1.621 | 142.91 | 121.69 | 5.042
2026-01-05 18:00 | 1767654000 | 1 | 1 | 2.001 | 138.45 | 123.01 | 4.526
2026-01-05 19:00 | 1767657600 | 1 | 1 | 2.102 | 134.76 | 118.06 | 5.145
2026-01-05 20:00 | 1767661200 | 1 | 1 | 2.117 | 130.41 | 114.05 | 5.074
2026-01-05 21:00 | 1767664800 | 1 | 1 | 2.1 | 154.01 | 130.66 | 7.187
2026-01-05 22:00 | 1767668400 | 1 | 0.9361 | 1.902 | 173.22 | 143.14 | 8.381
2026-01-05 23:00 | 1767672000 | 1 | 0.5917 | 1.173 | 173.26 | 141.82 | 5.406
2026-01-06 00:00 | 1767675600 | 1 | 0.6139 | 1.304 | 158.81 | 126.74 | 6.127
2026-01-06 01:00 | 1767679200 | 1 | 0.45 | 0.901 | 172.68 | 134.31 | 5.065
2026-01-06 02:00 | 1767682800 | 1 | 0.4306 | 0.901 | 173.05 | 129.46 | 5.751
2026-01-06 03:00 | 1767686400 | 1 | 0.6167 | 1.236 | 147.32 | 121.87 | 4.61
2026-01-06 04:00 | 1767690000 | 1 | 0.65 | 1.362 | 165.05 | 132.95 | 6.41
2026-01-06 05:00 | 1767693600 | 1 | 0.5556 | 1.16 | 171.55 | 131.16 | 6.854
2026-01-06 06:00 | 1767697200 | 1 | 0.475 | 0.945 | 157.6 | 127.46 | 4.172
2026-01-06 07:00 | 1767700800 | 1 | 0.5639 | 1.093 | 173.65 | 132.44 | 6.595
2026-01-06 08:00 | 1767704400 | 1 | 0.5083 | 1.011 | 167.63 | 132.52 | 5.201
2026-01-06 09:00 | 1767708000 | 1 | 0.5722 | 1.211 | 165.63 | 127.84 | 6.707
2026-01-06 10:00 | 1767711600 | 1 | 0.4167 | 0.83 | 162.64 | 126.88 | 4.348
2026-01-06 11:00 | 1767715200 | 1 | 0.3639 | 0.694 | 148.02 | 112.1 | 3.64
2026-01-06 12:00 | 1767718800 | 1 | 0.4 | 0.8 | 147.99 | 115.66 | 3.789
2026-01-06 13:00 | 1767722400 | 1 | 0.4333 | 0.824 | 144.66 | 111.55 | 3.996
2026-01-06 14:00 | 1767726000 | 1 | 0.3806 | 0.76 | 161.97 | 124.36 | 4.19
2026-01-06 15:00 | 1767729600 | 1 | 0.4333 | 0.939 | 164.97 | 121.76 | 5.945
2026-01-06 16:00 | 1767733200 | 1 | 0.3639 | 0.726 | 159.38 | 121.99 | 3.976
2026-01-06 17:00 | 1767736800 | 1 | 0.3417 | 0.679 | 169.07 | 132.64 | 3.621
2026-01-06 18:00 | 1767740400 | 1 | 0.2583 | 0.547 | 165.47 | 110.67 | 4.396
2026-01-06 19:00 | 1767744000 | 1 | 0.225 | 0.446 | 163.45 | 116.56 | 3.061
2026-01-06 20:00 | 1767747600 | 1 | 0.2361 | 0.493 | 162.25 | 106.26 | 4.043
2026-01-06 21:00 | 1767751200 | 1 | 0.45 | 0.898 | 143.24 | 114.37 | 3.798
2026-01-06 22:00 | 1767754800 | 1 | 0.5194 | 1.028 | 166.56 | 128.44 | 5.758
2026-01-06 23:00 | 1767758400 | 1 | 0.3361 | 0.678 | 166.89 | 121.45 | 4.515
2026-01-07 00:00 | 1767762000 | 0.9972 | 0.3733 | 0.746 | 160.77 | 123.63 | 4.051
2026-01-07 01:00 | 1767765600 | 1 | 0.6306 | 1.316 | 126.45 | 107.68 | 3.623
2026-01-07 02:00 | 1767769200 | 1 | 0.7694 | 1.498 | 151.69 | 125.09 | 5.84
2026-01-07 03:00 | 1767772800 | 1 | 0.3861 | 0.776 | 167.06 | 127.56 | 4.485
2026-01-07 04:00 | 1767776400 | 1 | 0.3528 | 0.726 | 167.55 | 120.94 | 4.956
2026-01-07 05:00 | 1767780000 | 1 | 0.25 | 0.499 | 158.75 | 119.09 | 2.9
2026-01-07 06:00 | 1767783600 | 1 | 0.6361 | 1.257 | 126.98 | 108.2 | 3.459
2026-01-07 07:00 | 1767787200 | 1 | 0.4528 | 0.905 | 166.41 | 129.57 | 4.879
2026-01-07 08:00 | 1767790800 | 1 | 0.4444 | 0.86 | 162.81 | 118.35 | 5.595
2026-01-07 12:00 | 1767805200 | 1 | 0.3806 | 0.758 | 149.28 | 118.56 | 3.411
2026-01-07 13:00 | 1767808800 | 1 | 0.5222 | 1.119 | 132.56 | 109.71 | 3.745
2026-01-07 14:00 | 1767812400 | 1 | 0.6389 | 1.278 | 144.38 | 120.49 | 4.473
2026-01-07 15:00 | 1767816000 | 1 | 0.3528 | 0.732 | 151.47 | 116.69 | 3.729
2026-01-07 16:00 | 1767819600 | 0.9611 | 0.5491 | 1.124 | 139.76 | 116.8 | 3.634
2026-01-07 17:00 | 1767823200 | 0.9722 | 0.4514 | 0.906 | 144.06 | 115.74 | 3.655
2026-01-07 18:00 | 1767826800 | 1 | 0.2667 | 0.584 | 148.8 | 108.33 | 3.462
2026-01-07 19:00 | 1767830400 | 1 | 0.2056 | 0.411 | 146.28 | 107.45 | 2.34
2026-01-07 20:00 | 1767834000 | 1 | 0.1944 | 0.491 | 145.54 | 97.62 | 3.428
2026-01-07 21:00 | 1767837600 | 1 | 0.1194 | 0.24 | 145.32 | 108.11 | 1.306
2026-01-07 22:00 | 1767841200 | 1 | 0.2333 | 0.516 | 142.03 | 96.57 | 3.432
2026-01-07 23:00 | 1767844800 | 1 | 0.2278 | 0.456 | 131.68 | 103.63 | 1.875
2026-01-08 00:00 | 1767848400 | 1 | 0.2444 | 0.589 | 158.31 | 108.16 | 4.33
2026-01-08 01:00 | 1767852000 | 1 | 0.2 | 0.401 | 158.85 | 108.7 | 2.946
2026-01-08 02:00 | 1767855600 | 1 | 0.2194 | 0.425 | 154.1 | 104.04 | 3.119
2026-01-08 03:00 | 1767859200 | 1 | 0.225 | 0.49 | 147.41 | 101.7 | 3.281
2026-01-08 04:00 | 1767862800 | 1 | 0.2667 | 0.537 | 137.91 | 108.47 | 2.313
2026-01-08 05:00 | 1767866400 | 1 | 0.3194 | 0.596 | 143.1 | 106.59 | 3.187
2026-01-08 06:00 | 1767870000 | 1 | 0.2111 | 0.429 | 155.81 | 111.28 | 2.784
2026-01-08 07:00 | 1767873600 | 1 | 0.3417 | 0.643 | 153.55 | 108.91 | 4.204
2026-01-08 08:00 | 1767877200 | 1 | 0.2639 | 0.523 | 145.78 | 108.92 | 2.825
2026-01-08 09:00 | 1767880800 | 1 | 0.3611 | 0.726 | 151.27 | 108.98 | 4.497
2026-01-08 10:00 | 1767884400 | 1 | 0.2056 | 0.411 | 154.25 | 110.02 | 2.665
2026-01-08 11:00 | 1767888000 | 1 | 0.1722 | 0.35 | 151.66 | 103.83 | 2.455
2026-01-08 12:00 | 1767891600 | 1 | 0.1833 | 0.334 | 154.17 | 102.16 | 2.535
2026-01-08 13:00 | 1767895200 | 1 | 0.1889 | 0.379 | 148.61 | 101.19 | 2.633
2026-01-08 14:00 | 1767898800 | 1 | 0.1806 | 0.32 | 145.92 | 96.93 | 2.288
2026-01-08 15:00 | 1767902400 | 1 | 0.4056 | 0.803 | 129.71 | 103.57 | 3.077
2026-01-08 16:00 | 1767906000 | 1 | 0.3 | 0.7 | 145.88 | 109.31 | 3.748
2026-01-08 17:00 | 1767909600 | 1 | 0.4444 | 0.889 | 141.91 | 114.54 | 3.565
2026-01-08 18:00 | 1767913200 | 1 | 0.1111 | 0.318 | 154.13 | 102.12 | 2.421
2026-01-08 20:00 | 1767920400 | 1 | 0.2528 | 0.466 | 149.22 | 93.55 | 3.801
2026-01-08 21:00 | 1767924000 | 1 | 0.0889 | 0.178 | 147.92 | 94.84 | 1.384
2026-01-08 22:00 | 1767927600 | 1 | 0.1806 | 0.32 | 149.73 | 95.44 | 2.549
2026-01-08 23:00 | 1767931200 | 1 | 0.2111 | 0.424 | 146.85 | 106.15 | 2.519
2026-01-09 00:00 | 1767934800 | 1 | 0.3167 | 0.602 | 128.31 | 101.05 | 2.4
2026-01-09 01:00 | 1767938400 | 1 | 0.4389 | 0.93 | 146.8 | 110.65 | 4.923
2026-01-09 02:00 | 1767942000 | 1 | 0.2111 | 0.419 | 159.79 | 114.22 | 2.8
2026-01-09 03:00 | 1767945600 | 1 | 0.2472 | 0.552 | 149.53 | 104.06 | 3.669
2026-01-09 04:00 | 1767949200 | 1 | 0.2278 | 0.459 | 142.2 | 108.6 | 2.25
2026-01-09 05:00 | 1767952800 | 1 | 0.4611 | 0.884 | 127.55 | 102.26 | 3.275
2026-01-09 06:00 | 1767956400 | 1 | 0.3222 | 0.668 | 155.5 | 112.52 | 4.207
2026-01-09 07:00 | 1767960000 | 1 | 0.2111 | 0.425 | 152.41 | 109.4 | 2.679
2026-01-09 08:00 | 1767963600 | 1 | 0.2611 | 0.535 | 145.56 | 102.53 | 3.369
2026-01-09 09:00 | 1767967200 | 1 | 0.2167 | 0.436 | 149.02 | 106.75 | 2.698
2026-01-09 10:00 | 1767970800 | 1 | 0.225 | 0.52 | 162.4 | 105.83 | 4.308
2026-01-09 11:00 | 1767974400 | 1 | 0.1056 | 0.212 | 161.18 | 110.38 | 1.579
2026-01-09 12:00 | 1767978000 | 1 | 0.2 | 0.401 | 158.11 | 107.82 | 2.956
2026-01-09 13:00 | 1767981600 | 1 | 0.2389 | 0.468 | 154.11 | 104.83 | 3.384
2026-01-09 14:00 | 1767985200 | 1 | 0.2361 | 0.577 | 142.76 | 101.97 | 3.447
2026-01-09 15:00 | 1767988800 | 1 | 0.0944 | 0.189 | 139.37 | 98.54 | 1.129
2026-01-09 16:00 | 1767992400 | 1 | 0.2778 | 0.523 | 139.35 | 97.13 | 3.231
2026-01-09 17:00 | 1767996000 | 1 | 0.2194 | 0.526 | 139.29 | 99.01 | 3.095
2026-01-09 18:00 | 1767999600 | 1 | 0.1167 | 0.236 | 134.22 | 100.65 | 1.162
2026-01-09 19:00 | 1768003200 | 1 | 0.1583 | 0.274 | 137.72 | 92.93 | 1.798
2026-01-09 20:00 | 1768006800 | 1 | 0.1694 | 0.295 | 132.39 | 86.82 | 1.973
2026-01-09 21:00 | 1768010400 | 1 | 0.0889 | 0.181 | 148.61 | 95.17 | 1.415
2026-01-09 22:00 | 1768014000 | 1 | 0.225 | 0.415 | 141.16 | 89.27 | 3.154
2026-01-09 23:00 | 1768017600 | 1 | 0.3694 | 0.741 | 150.16 | 118.92 | 3.39
2026-01-10 00:00 | 1768021200 | 1 | 0.3694 | 0.735 | 144.64 | 108.42 | 3.902
2026-01-10 01:00 | 1768024800 | 1 | 0.2889 | 0.581 | 151.82 | 114.93 | 3.14
2026-01-10 02:00 | 1768028400 | 1 | 0.1833 | 0.325 | 160.93 | 104.84 | 2.654
2026-01-10 03:00 | 1768032000 | 1 | 0.2056 | 0.412 | 156.71 | 108.91 | 2.882
2026-01-10 04:00 | 1768035600 | 1 | 0.2639 | 0.534 | 151.34 | 104.14 | 3.694
2026-01-10 05:00 | 1768039200 | 1 | 0.2222 | 0.449 | 145.24 | 108.12 | 2.44
2026-01-10 06:00 | 1768042800 | 1 | 0.3056 | 0.584 | 142.55 | 104.6 | 3.235
2026-01-10 07:00 | 1768046400 | 1 | 0.3194 | 0.598 | 147.23 | 107.72 | 3.46
2026-01-10 08:00 | 1768050000 | 1 | 0.3028 | 0.609 | 142.21 | 108.29 | 3.026
2026-01-10 09:00 | 1768053600 | 1 | 0.2611 | 0.477 | 146.67 | 106.55 | 2.804
2026-01-10 10:00 | 1768057200 | 1 | 0 | 0 |  |  | 0
2026-01-10 11:00 | 1768060800 | 1 | 0.2472 | 0.544 | 148.18 | 97.89 | 4.009
2026-01-10 12:00 | 1768064400 | 1 | 0.0944 | 0.19 | 144.49 | 96.78 | 1.326
2026-01-10 13:00 | 1768068000 | 1 | 0.1222 | 0.245 | 138.44 | 95.89 | 1.526
2026-01-10 14:00 | 1768071600 | 1 | 0.2778 | 0.5 | 148.44 | 102.82 | 3.346
2026-01-10 15:00 | 1768075200 | 1 | 0.2056 | 0.412 | 145.83 | 105.54 | 2.433
2026-01-10 16:00 | 1768078800 | 1 | 0.2833 | 0.527 | 162.91 | 104.69 | 4.5
2026-01-10 17:00 | 1768082400 | 1 | 0.0833 | 0.172 | 161.34 | 97.93 | 1.578
2026-01-10 18:00 | 1768086000 | 1 | 0 | 0 |  |  | 0
2026-01-10 19:00 | 1768089600 | 1 | 0.1639 | 0.285 | 162.76 | 91.66 | 2.974
2026-01-10 20:00 | 1768093200 | 1 | 0.0833 | 0.168 | 153.83 | 92.28 | 1.515
2026-01-10 21:00 | 1768096800 | 1 | 0.1889 | 0.474 | 155.08 | 96.08 | 4.099
2026-01-10 22:00 | 1768100400 | 1 | 0.0944 | 0.193 | 152.21 | 102.99 | 1.389
2026-01-10 23:00 | 1768104000 | 1 | 0.25 | 0.514 | 152.66 | 102.83 | 3.749
2026-01-11 00:00 | 1768107600 | 1 | 0.2222 | 0.449 | 145.47 | 108.56 | 2.423
2026-01-11 01:00 | 1768111200 | 1 | 0.2833 | 0.578 | 143.29 | 104.37 | 3.295
2026-01-11 02:00 | 1768114800 | 1 | 0.2972 | 0.557 | 153.13 | 107.82 | 3.696
2026-01-11 03:00 | 1768118400 | 1 | 0.2 | 0.403 | 163.74 | 110.34 | 3.152
2026-01-11 04:00 | 1768122000 | 1 | 0.175 | 0.306 | 162.93 | 102.7 | 2.702
2026-01-11 05:00 | 1768125600 | 1 | 0.1972 | 0.419 | 162.86 | 108 | 3.295
2026-01-11 06:00 | 1768129200 | 1 | 0.2306 | 0.425 | 160.45 | 100.56 | 3.729
2026-01-11 07:00 | 1768132800 | 1 | 0.1444 | 0.289 | 145.85 | 110.21 | 1.508
2026-01-11 08:00 | 1768136400 | 1 | 0.3417 | 0.649 | 145.59 | 104.69 | 3.892
2026-01-11 09:00 | 1768140000 | 1 | 0.1667 | 0.333 | 155.62 | 108.85 | 2.28
2026-01-11 10:00 | 1768143600 | 1 | 0.175 | 0.309 | 151.94 | 98.33 | 2.417
2026-01-11 11:00 | 1768147200 | 1 | 0.1889 | 0.381 | 141.74 | 100.71 | 2.277
2026-01-11 12:00 | 1768150800 | 1 | 0.0944 | 0.188 | 150.82 | 102.78 | 1.321
2026-01-11 13:00 | 1768154400 | 1 | 0.1778 | 0.324 | 163.08 | 100.65 | 2.954
2026-01-11 14:00 | 1768158000 | 1 | 0.15 | 0.319 | 159.52 | 95.16 | 2.949
2026-01-11 15:00 | 1768161600 | 1 | 0.2194 | 0.401 | 140.9 | 99.99 | 2.402
2026-01-11 16:00 | 1768165200 | 1 | 0.2167 | 0.433 | 156.83 | 109.81 | 2.982
2026-01-11 17:00 | 1768168800 | 1 | 0.2667 | 0.494 | 160.93 | 105.51 | 4.011
2026-01-11 18:00 | 1768172400 | 1 | 0 | 0 |  |  | 0
2026-01-11 19:00 | 1768176000 | 1 | 0.0278 | 0.043 | 137.14 | 69.99 | 0.427
2026-01-11 20:00 | 1768179600 | 1 | 0.0417 | 0.064 | 144.19 | 67.98 | 0.717
2026-01-11 21:00 | 1768183200 | 1 | 0.2278 | 0.437 | 134.99 | 92.65 | 2.71
2026-01-11 22:00 | 1768186800 | 1 | 0.2972 | 0.554 | 152.92 | 106.46 | 3.774
2026-01-11 23:00 | 1768190400 | 1 | 0.2056 | 0.409 | 163.33 | 110.67 | 3.155
2026-01-12 00:00 | 1768194000 | 1 | 0.1944 | 0.35 | 164.88 | 101.99 | 3.226
2026-01-12 01:00 | 1768197600 | 1 | 0.175 | 0.35 | 147.34 | 109.4 | 1.938
2026-01-12 02:00 | 1768201200 | 1 | 0.275 | 0.525 | 155.37 | 106.5 | 3.76
2026-01-12 03:00 | 1768204800 | 1 | 0.2389 | 0.468 | 152.59 | 109.41 | 2.952
2026-01-12 04:00 | 1768208400 | 1 | 0.2278 | 0.515 | 155.63 | 107.23 | 3.64
2026-01-12 05:00 | 1768212000 | 1 | 0.2167 | 0.437 | 156.04 | 110.95 | 2.887
2026-01-12 06:00 | 1768215600 | 1 | 0.3833 | 0.738 | 149.88 | 107.99 | 4.509
2026-01-12 07:00 | 1768219200 | 1 | 0.2639 | 0.611 | 165.94 | 112.9 | 4.745
2026-01-12 08:00 | 1768222800 | 1 | 0.3972 | 0.796 | 160.61 | 125.5 | 4.093
2026-01-12 09:00 | 1768226400 | 1 | 0.3417 | 0.649 | 158.99 | 114.63 | 4.217
2026-01-12 10:00 | 1768230000 | 1 | 0.3194 | 0.597 | 152.62 | 111.31 | 3.614
2026-01-12 11:00 | 1768233600 | 1 | 0.1889 | 0.382 | 158.04 | 105.43 | 2.938
2026-01-12 12:00 | 1768237200 | 1 | 0.2167 | 0.395 | 152.67 | 101.22 | 2.976
2026-01-12 13:00 | 1768240800 | 1 | 0.1861 | 0.373 | 157.84 | 111.95 | 2.51
2026-01-12 14:00 | 1768244400 | 1 | 0.2972 | 0.552 | 151.06 | 106.02 | 3.642
2026-01-12 15:00 | 1768248000 | 1 | 0.3611 | 0.827 | 157.3 | 112.59 | 5.416
2026-01-12 16:00 | 1768251600 | 1 | 0.2222 | 0.444 | 167.78 | 117.25 | 3.284
2026-01-12 17:00 | 1768255200 | 1 | 0.1806 | 0.322 | 167.57 | 108.31 | 2.797
2026-01-12 18:00 | 1768258800 | 1 | 0.1 | 0.2 | 163.88 | 107.59 | 1.654
2026-01-12 19:00 | 1768262400 | 1 | 0.2639 | 0.493 | 160.98 | 98.84 | 4.486
2026-01-12 20:00 | 1768266000 | 1 | 0.0944 | 0.195 | 157.74 | 98.69 | 1.683
2026-01-12 21:00 | 1768269600 | 1 | 0.1861 | 0.337 | 161.11 | 101.96 | 2.918
2026-01-12 22:00 | 1768273200 | 1 | 0.3139 | 0.701 | 144.64 | 104.13 | 4.161
2026-01-12 23:00 | 1768276800 | 1 | 0.2583 | 0.549 | 153.21 | 114.4 | 3.123
2026-01-13 00:00 | 1768280400 | 1 | 0.2472 | 0.503 | 161.58 | 106.18 | 4.079
2026-01-13 01:00 | 1768284000 | 1 | 0.1306 | 0.264 | 152.35 | 112.55 | 1.537
2026-01-13 02:00 | 1768287600 | 1 | 0.3028 | 0.566 | 151.08 | 107.47 | 3.596
2026-01-13 03:00 | 1768291200 | 1 | 0.2278 | 0.455 | 156.6 | 110.88 | 3.048
2026-01-13 04:00 | 1768294800 | 1 | 0.2917 | 0.543 | 150.95 | 105.22 | 3.637
2026-01-13 05:00 | 1768298400 | 1 | 0.1917 | 0.341 | 163.63 | 105.77 | 2.888
2026-01-13 06:00 | 1768302000 | 1 | 0.2 | 0.406 | 162.21 | 108.35 | 3.2
2026-01-13 07:00 | 1768305600 | 1 | 0.1806 | 0.324 | 159.65 | 102.76 | 2.689
2026-01-13 08:00 | 1768309200 | 1 | 0.2806 | 0.565 | 160.71 | 118.08 | 3.532
2026-01-13 09:00 | 1768312800 | 1 | 0.275 | 0.511 | 158.28 | 106.58 | 3.871
2026-01-13 10:00 | 1768316400 | 1 | 0.1889 | 0.378 | 158.14 | 107.55 | 2.801
2026-01-13 11:00 | 1768320000 | 1 | 0.2111 | 0.418 | 155.85 | 106.41 | 3.025
2026-01-13 12:00 | 1768323600 | 1 | 0.2222 | 0.411 | 147.43 | 101.15 | 2.788
2026-01-13 13:00 | 1768327200 | 1 | 0.2278 | 0.423 | 148.53 | 105.34 | 2.672
2026-01-13 14:00 | 1768330800 | 1 | 0.1778 | 0.358 | 144.01 | 98.81 | 2.37
2026-01-13 15:00 | 1768334400 | 1 | 0.1694 | 0.359 | 144.51 | 102.97 | 2.183
2026-01-13 16:00 | 1768338000 | 1 | 0.3528 | 0.778 | 159.98 | 118.63 | 4.714
2026-01-13 17:00 | 1768341600 | 1 | 0.1361 | 0.249 | 159.36 | 96.23 | 2.288
2026-01-13 18:00 | 1768345200 | 1 | 0.1167 | 0.218 | 156.45 | 101.76 | 1.747
2026-01-13 19:00 | 1768348800 | 1 | 0.0833 | 0.166 | 147.51 | 92.22 | 1.346
2026-01-13 20:00 | 1768352400 | 1 | 0.1583 | 0.284 | 150.27 | 94.7 | 2.317
2026-01-13 21:00 | 1768356000 | 1 | 0.0889 | 0.175 | 150.45 | 93.73 | 1.456
2026-01-13 22:00 | 1768359600 | 1 | 0.2694 | 0.545 | 142.3 | 100.65 | 3.31
2026-01-13 23:00 | 1768363200 | 1 | 0.2278 | 0.455 | 151.47 | 110.55 | 2.731
2026-01-14 00:00 | 1768366800 | 0.9972 | 0.2925 | 0.547 | 165.69 | 109.16 | 4.514
2026-01-14 01:00 | 1768370400 | 1 | 0.1944 | 0.39 | 163.96 | 109.53 | 3.104
2026-01-14 02:00 | 1768374000 | 1 | 0.2556 | 0.468 | 139.83 | 100.34 | 2.703
2026-01-14 03:00 | 1768377600 | 1 | 0.2583 | 0.527 | 153.65 | 112.16 | 3.19
2026-01-14 04:00 | 1768381200 | 1 | 0.1861 | 0.33 | 155.19 | 103.59 | 2.493
2026-01-14 05:00 | 1768384800 | 1 | 0.2111 | 0.437 | 149.05 | 107.99 | 2.627
2026-01-14 06:00 | 1768388400 | 1 | 0.2278 | 0.461 | 144.45 | 108.74 | 2.406
2026-01-14 07:00 | 1768392000 | 1 | 0.25 | 0.564 | 143.77 | 103.93 | 3.295
2026-01-14 08:00 | 1768395600 | 1 | 0.2 | 0.406 | 141.12 | 103.21 | 2.253
2026-01-14 09:00 | 1768399200 | 1 | 0.2611 | 0.531 | 140.96 | 99.02 | 3.267
2026-01-14 10:00 | 1768402800 | 1 | 0.2167 | 0.435 | 139.61 | 103.84 | 2.278
2026-01-14 11:00 | 1768406400 | 1 | 0.3556 | 0.664 | 137.59 | 103.84 | 3.282
2026-01-14 12:00 | 1768410000 | 1 | 0.2167 | 0.441 | 135.68 | 104.36 | 2.018
2026-01-14 13:00 | 1768413600 | 1 | 0.2389 | 0.541 | 141.03 | 100.2 | 3.239
2026-01-14 14:00 | 1768417200 | 1 | 0.2 | 0.401 | 138.99 | 102.36 | 2.154
2026-01-14 15:00 | 1768420800 | 1 | 0.2167 | 0.437 | 139.94 | 104.76 | 2.249
2026-01-14 16:00 | 1768424400 | 1 | 0.2722 | 0.568 | 145.18 | 103.9 | 3.425
2026-01-14 17:00 | 1768428000 | 1 | 0.1028 | 0.206 | 140.1 | 101.38 | 1.169
2026-01-14 18:00 | 1768431600 | 1 | 0.2583 | 0.527 | 138.95 | 99.68 | 3.031
2026-01-14 19:00 | 1768435200 | 1 | 0.2139 | 0.433 | 135.17 | 102.16 | 2.092
2026-01-14 20:00 | 1768438800 | 1 | 0.2944 | 0.55 | 133.49 | 98.82 | 2.795
2026-01-14 21:00 | 1768442400 | 1 | 0.0917 | 0.185 | 134.97 | 94.9 | 1.086
2026-01-14 22:00 | 1768446000 | 1 | 0.2611 | 0.53 | 134.73 | 94.39 | 3.134
2026-01-14 23:00 | 1768449600 | 1 | 0.3861 | 0.782 | 124.07 | 101.24 | 2.616
2026-01-15 00:00 | 1768453200 | 1 | 0.3306 | 0.753 | 126.43 | 101.47 | 2.753
2026-01-15 01:00 | 1768456800 | 1 | 0.4139 | 0.834 | 127.27 | 108.01 | 2.355
2026-01-15 02:00 | 1768460400 | 1 | 0.575 | 1.126 | 126.88 | 104.49 | 3.675
2026-01-15 03:00 | 1768464000 | 1 | 0.2556 | 0.515 | 149.31 | 114.14 | 2.653
2026-01-15 04:00 | 1768467600 | 1 | 0.3944 | 0.852 | 125.88 | 100.38 | 3.183
2026-01-15 05:00 | 1768471200 | 1 | 0.2556 | 0.594 | 135.1 | 102.9 | 2.801
2026-01-15 06:00 | 1768474800 | 1 | 0.35 | 0.702 | 136.32 | 109.32 | 2.778
2026-01-15 07:00 | 1768478400 | 1 | 0.25 | 0.589 | 144.97 | 104.41 | 3.474
2026-01-15 08:00 | 1768482000 | 1 | 0.2 | 0.405 | 142.12 | 103.96 | 2.253
2026-01-15 09:00 | 1768485600 | 1 | 0.2722 | 0.507 | 136.03 | 98.06 | 2.822
2026-01-15 10:00 | 1768489200 | 1 | 0.2278 | 0.456 | 128.44 | 100.73 | 1.85
2026-01-15 11:00 | 1768492800 | 1 | 0.3861 | 0.776 | 128.7 | 105.19 | 2.674
2026-01-15 12:00 | 1768496400 | 1 | 0.4194 | 0.795 | 127.34 | 101.62 | 2.994
2026-01-15 13:00 | 1768500000 | 1 | 0.4083 | 0.826 | 130.9 | 108.91 | 2.656
2026-01-15 14:00 | 1768503600 | 1 | 0.3694 | 0.817 | 137.96 | 106.08 | 3.817
2026-01-15 15:00 | 1768507200 | 1 | 0.2167 | 0.436 | 144.13 | 106.3 | 2.414
2026-01-15 16:00 | 1768510800 | 1 | 0.2056 | 0.449 | 142.36 | 100.96 | 2.725
2026-01-15 17:00 | 1768514400 | 1 | 0.1472 | 0.328 | 140.7 | 99.72 | 1.972
2026-01-15 18:00 | 1768518000 | 1 | 0.1778 | 0.362 | 139.98 | 98.23 | 2.205
2026-01-15 19:00 | 1768521600 | 1 | 0.1778 | 0.317 | 138.9 | 91.82 | 2.187
2026-01-15 20:00 | 1768525200 | 1 | 0.3194 | 0.644 | 121.65 | 97.47 | 2.283
2026-01-15 21:00 | 1768528800 | 1 | 0.3361 | 0.765 | 140.29 | 107.77 | 3.643
2026-01-15 22:00 | 1768532400 | 1 | 0.3778 | 0.772 | 137.64 | 110.21 | 3.101
2026-01-15 23:00 | 1768536000 | 1 | 0.35 | 0.664 | 133.71 | 104.48 | 2.843
2026-01-16 00:00 | 1768539600 | 1 | 0.375 | 0.766 | 132.61 | 108.17 | 2.731
2026-01-16 01:00 | 1768543200 | 1 | 0.5278 | 1.019 | 145.27 | 112.09 | 4.954
2026-01-16 02:00 | 1768546800 | 1 | 0.2222 | 0.45 | 156.02 | 115.81 | 2.638
2026-01-16 03:00 | 1768550400 | 1 | 0.3083 | 0.576 | 149.91 | 108.99 | 3.452
2026-01-16 04:00 | 1768554000 | 1 | 0.4944 | 0.923 | 138.8 | 112.9 | 3.504
2026-01-16 05:00 | 1768557600 | 1 | 0.4889 | 1.08 | 155.07 | 119.41 | 5.639
2026-01-16 06:00 | 1768561200 | 1 | 0.2806 | 0.596 | 168.6 | 118.47 | 4.379
2026-01-16 07:00 | 1768564800 | 1 | 0.3 | 0.6 | 158.91 | 114.23 | 3.925
2026-01-16 08:00 | 1768568400 | 1 | 0.4167 | 0.794 | 161.57 | 119.49 | 4.88
2026-01-16 09:00 | 1768572000 | 1 | 0.4222 | 0.845 | 159.51 | 123.06 | 4.513
2026-01-16 10:00 | 1768575600 | 1 | 0.4306 | 0.951 | 158.83 | 119.99 | 5.411
2026-01-16 11:00 | 1768579200 | 1 | 0.5639 | 1.165 | 158.03 | 125.38 | 5.514
2026-01-16 12:00 | 1768582800 | 1 | 0.4556 | 0.914 | 160.84 | 127.35 | 4.482
2026-01-16 13:00 | 1768586400 | 1 | 0.4389 | 0.982 | 151.79 | 119.22 | 4.686
2026-01-16 14:00 | 1768590000 | 1 | 0.5833 | 1.102 | 159.26 | 124.24 | 5.657
2026-01-16 15:00 | 1768593600 | 1 | 0.4472 | 0.898 | 164.04 | 129.37 | 4.561
2026-01-16 16:00 | 1768597200 | 1 | 0.7306 | 1.477 | 158.33 | 127.55 | 6.651
2026-01-16 17:00 | 1768600800 | 1 | 1 | 2.104 | 150.07 | 127.98 | 6.812
2026-01-16 18:00 | 1768604400 | 1 | 0.8944 | 1.791 | 149.23 | 128.63 | 5.407
2026-01-16 19:00 | 1768608000 | 1 | 0.7778 | 1.635 | 144.49 | 121.49 | 5.507
2026-01-16 20:00 | 1768611600 | 1 | 0.9333 | 1.98 | 143.06 | 121.18 | 6.347
2026-01-16 21:00 | 1768615200 | 1 | 0.6556 | 1.316 | 166.19 | 132.96 | 6.407
2026-01-16 22:00 | 1768618800 | 1 | 0.7222 | 1.529 | 158.27 | 129.45 | 6.456
2026-01-16 23:00 | 1768622400 | 1 | 0.7528 | 1.617 | 164.74 | 132.42 | 7.659
2026-01-17 00:00 | 1768626000 | 1 | 0.6278 | 1.312 | 166.35 | 132.21 | 6.562
2026-01-17 01:00 | 1768629600 | 1 | 0.7889 | 1.698 | 153.91 | 126.58 | 6.8
2026-01-17 02:00 | 1768633200 | 1 | 0.7472 | 1.457 | 168.31 | 133.03 | 7.534
2026-01-17 03:00 | 1768636800 | 1 | 0.5083 | 1.033 | 165.35 | 131.34 | 5.151
2026-01-17 04:00 | 1768640400 | 1 | 0.5056 | 1.112 | 162.39 | 127.41 | 5.701
2026-01-17 05:00 | 1768644000 | 1 | 0.625 | 1.264 | 160.06 | 125.91 | 6.323
2026-01-17 06:00 | 1768647600 | 1 | 0.7139 | 1.388 | 158.06 | 124.95 | 6.733
2026-01-17 07:00 | 1768651200 | 1 | 0.4917 | 1.028 | 164.62 | 125.71 | 5.861
2026-01-17 08:00 | 1768654800 | 1 | 0.3444 | 0.692 | 161.57 | 126.71 | 3.534
2026-01-17 09:00 | 1768658400 | 1 | 0.4222 | 0.961 | 155.15 | 115.29 | 5.613
2026-01-17 10:00 | 1768662000 | 1 | 0.4361 | 0.836 | 157.14 | 114.68 | 5.202
2026-01-17 11:00 | 1768665600 | 1 | 0.3639 | 0.687 | 162.67 | 114.09 | 4.888
2026-01-17 12:00 | 1768669200 | 1 | 0.2861 | 0.558 | 166.3 | 116.46 | 4.065
2026-01-17 13:00 | 1768672800 | 1 | 0.3139 | 0.605 | 165.88 | 117.43 | 4.297
2026-01-17 14:00 | 1768676400 | 1 | 0.2028 | 0.363 | 164.43 | 111.34 | 2.822
2026-01-17 15:00 | 1768680000 | 1 | 0.2806 | 0.517 | 160.61 | 97.48 | 4.782
2026-01-17 16:00 | 1768683600 | 1 | 0.1 | 0.202 | 158.22 | 102.87 | 1.638
2026-01-17 17:00 | 1768687200 | 1 | 0.5194 | 1.139 | 161.36 | 119.68 | 6.959
2026-01-17 18:00 | 1768690800 | 1 | 0.3139 | 0.584 | 158.45 | 109.97 | 4.149
2026-01-17 19:00 | 1768694400 | 1 | 0.2944 | 0.563 | 151.81 | 106.85 | 3.702
2026-01-17 20:00 | 1768698000 | 1 | 0.4194 | 0.837 | 149.46 | 115.05 | 4.223
2026-01-17 21:00 | 1768701600 | 1 | 0.2889 | 0.543 | 155.33 | 106.11 | 3.918
2026-01-17 22:00 | 1768705200 | 1 | 0.3 | 0.608 | 159.95 | 118.86 | 3.639
2026-01-17 23:00 | 1768708800 | 1 | 0.5972 | 1.301 | 151.3 | 121.66 | 5.651
2026-01-18 00:00 | 1768712400 | 1 | 0.6639 | 1.442 | 152.22 | 123.29 | 6.112
2026-01-18 01:00 | 1768716000 | 1 | 0.5194 | 1.155 | 161.88 | 126.24 | 6.021
2026-01-18 02:00 | 1768719600 | 1 | 0.5611 | 1.224 | 153.8 | 124.03 | 5.337
2026-01-18 03:00 | 1768723200 | 1 | 0.6417 | 1.29 | 155.89 | 126.28 | 5.595
2026-01-18 04:00 | 1768726800 | 1 | 0.4778 | 1.061 | 166.8 | 125.12 | 6.479
2026-01-18 05:00 | 1768730400 | 1 | 0.5472 | 1.019 | 155.24 | 120.49 | 5.186
2026-01-18 06:00 | 1768734000 | 1 | 0.5611 | 1.134 | 151.39 | 125.71 | 4.257
2026-01-18 07:00 | 1768737600 | 1 | 0.6444 | 1.324 | 158.42 | 124.77 | 6.524
2026-01-18 08:00 | 1768741200 | 1 | 0.5111 | 0.989 | 153.4 | 117.2 | 5.246
2026-01-18 09:00 | 1768744800 | 1 | 0.3444 | 0.69 | 156.74 | 121.18 | 3.594
2026-01-18 10:00 | 1768748400 | 1 | 0.2694 | 0.576 | 161.08 | 108.79 | 4.412
2026-01-18 11:00 | 1768752000 | 1 | 0.2278 | 0.458 | 162.61 | 112.35 | 3.376
2026-01-18 12:00 | 1768755600 | 1 | 0.2056 | 0.414 | 145.6 | 109.26 | 2.204
2026-01-18 13:00 | 1768759200 | 1 | 0.1194 | 0.226 | 146.23 | 89.14 | 1.887
2026-01-18 14:00 | 1768762800 | 1 | 0.2 | 0.407 | 149.51 | 102.33 | 2.793
2026-01-18 15:00 | 1768766400 | 1 | 0.175 | 0.311 | 162.3 | 102.65 | 2.713
2026-01-18 16:00 | 1768770000 | 1 | 0 | 0 |  |  | 0
2026-01-18 17:00 | 1768773600 | 1 | 0.1694 | 0.303 | 159.79 | 91.26 | 3.03
2026-01-18 18:00 | 1768777200 | 1 | 0.0944 | 0.189 | 159.43 | 105.16 | 1.502
2026-01-18 19:00 | 1768780800 | 1 | 0.175 | 0.307 | 162.49 | 96.26 | 2.979
2026-01-18 20:00 | 1768784400 | 1 | 0.2111 | 0.421 | 166.32 | 111.07 | 3.409
2026-01-18 21:00 | 1768788000 | 1 | 0.2861 | 0.536 | 168.3 | 109.67 | 4.597
2026-01-18 22:00 | 1768791600 | 1 | 0.1583 | 0.316 | 164.69 | 109.14 | 2.568
2026-01-18 23:00 | 1768795200 | 1 | 0.3694 | 0.726 | 144.69 | 111.01 | 3.58
2026-01-19 00:00 | 1768798800 | 1 | 0.2806 | 0.589 | 160.04 | 112.07 | 4.134
2026-01-19 01:00 | 1768802400 | 1 | 0.2444 | 0.481 | 151.96 | 112.16 | 2.805
2026-01-19 02:00 | 1768806000 | 1 | 0.3028 | 0.573 | 150.47 | 110.49 | 3.353
2026-01-19 03:00 | 1768809600 | 1 | 0.3389 | 0.751 | 158.01 | 111.39 | 5.13
2026-01-19 05:00 | 1768816800 | 1 | 0.2611 | 0.492 | 163.5 | 114.03 | 3.547
2026-01-19 06:00 | 1768820400 | 1 | 0.2167 | 0.439 | 164.14 | 114.38 | 3.2
2026-01-19 07:00 | 1768824000 | 1 | 0.5028 | 0.985 | 163.74 | 122.96 | 5.888
2026-01-19 08:00 | 1768827600 | 1 | 0.2611 | 0.522 | 160.67 | 121.31 | 3.009
2026-01-19 09:00 | 1768831200 | 1 | 0.3306 | 0.621 | 160.21 | 113.97 | 4.209
2026-01-19 10:00 | 1768834800 | 1 | 0.2167 | 0.437 | 157.89 | 114.01 | 2.804
2026-01-19 11:00 | 1768838400 | 1 | 0.2028 | 0.499 | 157.39 | 104.17 | 3.894
2026-01-19 12:00 | 1768842000 | 1 | 0.2167 | 0.433 | 148.8 | 109.28 | 2.51
2026-01-19 13:00 | 1768845600 | 1 | 0.3278 | 0.615 | 147.17 | 108.62 | 3.473
2026-01-19 14:00 | 1768849200 | 1 | 0.3056 | 0.618 | 154.27 | 113.03 | 3.716
2026-01-19 15:00 | 1768852800 | 1 | 0.2778 | 0.658 | 163.2 | 113.79 | 4.762
2026-01-19 16:00 | 1768856400 | 1 | 0.1056 | 0.211 | 168 | 115.66 | 1.62
2026-01-19 17:00 | 1768860000 | 1 | 0.1639 | 0.286 | 164.77 | 95.8 | 2.888
2026-01-19 18:00 | 1768863600 | 1 | 0.0861 | 0.172 | 160.19 | 98.2 | 1.563
2026-01-19 19:00 | 1768867200 | 1 | 0.2833 | 0.529 | 163.49 | 104.46 | 4.571
2026-01-19 20:00 | 1768870800 | 1 | 0.2278 | 0.464 | 162.48 | 116.65 | 3.103
2026-01-19 21:00 | 1768874400 | 1 | 0.2528 | 0.499 | 159.87 | 117.56 | 3.089
2026-01-19 22:00 | 1768878000 | 1 | 0.5056 | 0.967 | 153.28 | 116.89 | 5.152
2026-01-19 23:00 | 1768881600 | 1 | 0.2583 | 0.519 | 160.58 | 121.67 | 2.958
2026-01-20 00:00 | 1768885200 | 1 | 0.4528 | 0.968 | 145.41 | 113.67 | 4.505
2026-01-20 01:00 | 1768888800 | 1 | 0.3 | 0.69 | 161.78 | 114.78 | 4.751
2026-01-20 02:00 | 1768892400 | 1 | 0.3417 | 0.683 | 159.09 | 124.02 | 3.51
2026-01-20 03:00 | 1768896000 | 1 | 0.2667 | 0.621 | 157.13 | 115.39 | 3.792
2026-01-20 04:00 | 1768899600 | 1 | 0.375 | 0.753 | 164.19 | 123.16 | 4.516
2026-01-20 05:00 | 1768903200 | 1 | 0.2556 | 0.591 | 167.12 | 115.74 | 4.449
2026-01-20 06:00 | 1768906800 | 1 | 0.3389 | 0.677 | 158.22 | 119.89 | 3.803
2026-01-20 07:00 | 1768910400 | 1 | 0.3861 | 0.77 | 161.07 | 121.6 | 4.456
2026-01-20 08:00 | 1768914000 | 1 | 0.2389 | 0.479 | 164.6 | 119.77 | 3.149
2026-01-20 09:00 | 1768917600 | 1 | 0.425 | 0.806 | 165.16 | 115.8 | 5.824
2026-01-20 10:00 | 1768921200 | 1 | 0.2306 | 0.461 | 159.79 | 115.69 | 2.981
2026-01-20 11:00 | 1768924800 | 1 | 0.1694 | 0.296 | 155.05 | 96.86 | 2.522
2026-01-20 12:00 | 1768928400 | 1 | 0.3583 | 0.716 | 150.3 | 111.22 | 4.101
2026-01-20 13:00 | 1768932000 | 1 | 0.3472 | 0.686 | 167.6 | 120.25 | 4.761
2026-01-20 14:00 | 1768935600 | 1 | 0.4111 | 0.818 | 156.7 | 120.42 | 4.344
2026-01-20 15:00 | 1768939200 | 1 | 0.3667 | 0.696 | 164.6 | 121.04 | 4.43
2026-01-20 16:00 | 1768942800 | 1 | 0.5139 | 0.993 | 168.59 | 124.92 | 6.345
2026-01-20 17:00 | 1768946400 | 1 | 0.4667 | 0.941 | 160.67 | 126.86 | 4.659
2026-01-20 18:00 | 1768950000 | 1 | 0.4472 | 0.883 | 160.97 | 124.51 | 4.715
2026-01-20 19:00 | 1768953600 | 1 | 0.3194 | 0.602 | 150.7 | 108.95 | 3.669
2026-01-20 20:00 | 1768957200 | 1 | 0.4417 | 0.845 | 151.49 | 111.56 | 4.941
2026-01-20 21:00 | 1768960800 | 1 | 0.4444 | 0.918 | 164.18 | 125.49 | 5.203
2026-01-20 22:00 | 1768964400 | 1 | 0.5194 | 1.045 | 163.06 | 126.56 | 5.59
2026-01-20 23:00 | 1768968000 | 1 | 0.5833 | 1.124 | 164.92 | 129.66 | 5.805
2026-01-21 00:00 | 1768971600 | 0.9972 | 0.6017 | 1.158 | 168.87 | 129.82 | 6.608
2026-01-21 01:00 | 1768975200 | 1 | 0.5444 | 1.083 | 163.92 | 131.68 | 5.115
2026-01-21 02:00 | 1768978800 | 1 | 0.5278 | 1.013 | 167.81 | 127.06 | 6.052
2026-01-21 03:00 | 1768982400 | 1 | 0.4833 | 1.072 | 161.29 | 128.01 | 5.225
2026-01-21 04:00 | 1768986000 | 1 | 0.6056 | 1.166 | 169.42 | 130.14 | 6.701
2026-01-21 05:00 | 1768989600 | 1 | 0.5417 | 1.174 | 159.39 | 126.02 | 5.738
2026-01-21 06:00 | 1768993200 | 1 | 0.5 | 1.005 | 166.35 | 131.56 | 5.123
2026-01-21 07:00 | 1768996800 | 1 | 0.5028 | 0.955 | 169.62 | 130.09 | 5.533
2026-01-21 08:00 | 1769000400 | 1 | 0.5194 | 1.004 | 166.14 | 124.42 | 6.136
2026-01-21 09:00 | 1769004000 | 1 | 0.4583 | 0.912 | 158.09 | 124.64 | 4.469
2026-01-21 10:00 | 1769007600 | 1 | 0.4806 | 0.917 | 155.9 | 120.23 | 4.775
2026-01-21 11:00 | 1769011200 | 1 | 0.4611 | 0.871 | 150.05 | 114.68 | 4.515
2026-01-21 12:00 | 1769014800 | 0.9528 | 0.4461 | 0.871 | 144.51 | 116.95 | 3.349
2026-01-21 13:00 | 1769018400 | 1 | 0.3778 | 0.748 | 156.37 | 117.72 | 4.239
2026-01-21 14:00 | 1769022000 | 1 | 0.325 | 0.608 | 157.72 | 112.26 | 4.044
2026-01-21 15:00 | 1769025600 | 1 | 0.2583 | 0.519 | 156.56 | 118.91 | 2.858
2026-01-21 16:00 | 1769029200 | 1 | 0.4694 | 0.891 | 164.4 | 120.11 | 5.772
2026-01-21 17:00 | 1769032800 | 1 | 0.4417 | 0.929 | 157.22 | 121.26 | 4.893
2026-01-21 18:00 | 1769036400 | 1 | 0.4556 | 0.899 | 152.43 | 120.24 | 4.238
2026-01-21 19:00 | 1769040000 | 1 | 0.4972 | 0.947 | 147.94 | 116.92 | 4.305
2026-01-21 20:00 | 1769043600 | 1 | 0.5889 | 1.142 | 149.5 | 118.31 | 5.219
2026-01-21 21:00 | 1769047200 | 1 | 0.4639 | 0.932 | 156.5 | 124.51 | 4.366
2026-01-21 22:00 | 1769050800 | 1 | 0.4917 | 0.935 | 158.87 | 120.52 | 5.256
2026-01-21 23:00 | 1769054400 | 1 | 0.3583 | 0.721 | 156.54 | 125.79 | 3.245
2026-01-22 00:00 | 1769058000 | 1 | 0.475 | 1.079 | 154.77 | 119.73 | 5.539
2026-01-22 01:00 | 1769061600 | 1 | 0.4917 | 1.053 | 152.3 | 119.47 | 5.064
2026-01-22 02:00 | 1769065200 | 1 | 0.4361 | 0.944 | 154.72 | 118.2 | 5.054
2026-01-22 03:00 | 1769068800 | 1 | 0.3889 | 0.731 | 153.66 | 117.71 | 3.843
2026-01-22 04:00 | 1769072400 | 1 | 0.45 | 1 | 152.41 | 117.25 | 5.145
2026-01-22 05:00 | 1769076000 | 1 | 0.3028 | 0.658 | 160.26 | 116.15 | 4.256
2026-01-22 06:00 | 1769079600 | 1 | 0.375 | 0.75 | 159.2 | 120.61 | 4.234
2026-01-22 07:00 | 1769083200 | 1 | 0.3833 | 0.725 | 153.17 | 114.21 | 4.137
2026-01-22 08:00 | 1769086800 | 1 | 0.4917 | 0.956 | 148.34 | 116.71 | 4.418
2026-01-22 09:00 | 1769090400 | 1 | 0.4167 | 0.942 | 144.95 | 111.83 | 4.569
2026-01-22 10:00 | 1769094000 | 1 | 0.3639 | 0.731 | 143 | 112.54 | 3.261
2026-01-22 11:00 | 1769097600 | 0.9528 | 0.309 | 0.568 | 141.13 | 97.59 | 3.452
2026-01-22 12:00 | 1769101200 | 1 | 0.2722 | 0.504 | 145.22 | 98.24 | 3.457
2026-01-22 13:00 | 1769104800 | 1 | 0.2139 | 0.428 | 147.79 | 108.73 | 2.45
2026-01-22 14:00 | 1769108400 | 1 | 0.2833 | 0.563 | 151.51 | 106.96 | 3.674
2026-01-22 15:00 | 1769112000 | 1 | 0.2972 | 0.562 | 142.18 | 105.3 | 3.035
2026-01-22 16:00 | 1769115600 | 1 | 0.2278 | 0.461 | 149.58 | 111.85 | 2.54
2026-01-22 17:00 | 1769119200 | 1 | 0.3361 | 0.716 | 141.12 | 104.04 | 3.887
2026-01-22 18:00 | 1769122800 | 1 | 0.2083 | 0.397 | 138.53 | 102.56 | 2.088
2026-01-22 19:00 | 1769126400 | 1 | 0.4139 | 0.868 | 136.14 | 109.52 | 3.385
2026-01-22 20:00 | 1769130000 | 1 | 0.2611 | 0.487 | 142.15 | 100.72 | 2.954
2026-01-22 21:00 | 1769133600 | 1 | 0.2917 | 0.542 | 153.85 | 103.7 | 3.982
2026-01-22 22:00 | 1769137200 | 1 | 0.2722 | 0.546 | 143.08 | 112.69 | 2.432
2026-01-22 23:00 | 1769140800 | 1 | 0.3833 | 0.777 | 160.03 | 115.72 | 5.044
2026-01-23 00:00 | 1769144400 | 1 | 0.3972 | 0.786 | 155.87 | 117.45 | 4.413
2026-01-23 01:00 | 1769148000 | 1 | 0.4417 | 0.857 | 148.12 | 115.34 | 4.117
2026-01-23 02:00 | 1769151600 | 1 | 0.4722 | 0.946 | 147.41 | 118.49 | 4.005
2026-01-23 03:00 | 1769155200 | 1 | 0.4889 | 1.038 | 153.21 | 124.3 | 4.399
2026-01-23 04:00 | 1769158800 | 1 | 0.4056 | 0.921 | 159.34 | 119.59 | 5.354
2026-01-23 05:00 | 1769162400 | 1 | 0.2917 | 0.69 | 152.51 | 114.95 | 3.799
2026-01-23 06:00 | 1769166000 | 1 | 0.4583 | 0.99 | 157.74 | 121.06 | 5.315
2026-01-23 07:00 | 1769169600 | 1 | 0.3861 | 0.808 | 160.1 | 120.66 | 4.671
2026-01-23 08:00 | 1769173200 | 1 | 0.2944 | 0.583 | 160.12 | 124.96 | 3.005
2026-01-23 09:00 | 1769176800 | 1 | 0.4 | 0.753 | 156.72 | 115.01 | 4.604
2026-01-23 10:00 | 1769180400 | 1 | 0.2778 | 0.655 | 151.59 | 111.5 | 3.847
2026-01-23 11:00 | 1769184000 | 1 | 0.3056 | 0.602 | 144.23 | 105.62 | 3.407
2026-01-23 12:00 | 1769187600 | 1 | 0.5194 | 1.125 | 139 | 112.35 | 4.386
2026-01-23 13:00 | 1769191200 | 1 | 0.5778 | 1.158 | 131.71 | 113.49 | 3.09
2026-01-23 14:00 | 1769194800 | 1 | 0.7139 | 1.548 | 134.52 | 114.03 | 4.648
2026-01-23 15:00 | 1769198400 | 1 | 0.6833 | 1.478 | 145.53 | 121.76 | 5.148
2026-01-23 16:00 | 1769202000 | 1 | 0.6444 | 1.4 | 148.52 | 122.13 | 5.41
2026-01-23 17:00 | 1769205600 | 1 | 0.6278 | 1.244 | 158.98 | 126.03 | 6.008
2026-01-23 18:00 | 1769209200 | 1 | 0.5 | 1.107 | 154.93 | 121.17 | 5.477
2026-01-23 19:00 | 1769212800 | 1 | 0.5028 | 1.027 | 150.48 | 117.98 | 4.891
2026-01-23 20:00 | 1769216400 | 1 | 0.5972 | 1.298 | 137.44 | 116.71 | 3.938
2026-01-23 21:00 | 1769220000 | 1 | 0.5 | 1.077 | 145.71 | 113.82 | 5.031
2026-01-23 22:00 | 1769223600 | 1 | 0.75 | 1.628 | 144.85 | 119.4 | 6.068
2026-01-23 23:00 | 1769227200 | 1 | 0.8944 | 1.903 | 153.24 | 128.15 | 6.997
2026-01-24 00:00 | 1769230800 | 1 | 1 | 2.13 | 143.16 | 122.43 | 6.468
2026-01-24 01:00 | 1769234400 | 1 | 0.9 | 1.912 | 160.22 | 133.02 | 7.623
2026-01-24 02:00 | 1769238000 | 1 | 1 | 2.125 | 138.12 | 120.43 | 5.51
2026-01-24 03:00 | 1769241600 | 1 | 1 | 2.123 | 157.56 | 131.61 | 8.073
2026-01-24 04:00 | 1769245200 | 1 | 1 | 2.134 | 145.16 | 125.51 | 6.146
2026-01-24 05:00 | 1769248800 | 1 | 1 | 2.13 | 150.65 | 127.69 | 7.167
2026-01-24 06:00 | 1769252400 | 1 | 1 | 2.123 | 155.38 | 131.01 | 7.582
2026-01-24 07:00 | 1769256000 | 1 | 1 | 2.28 | 133.65 | 115.97 | 5.905
2026-01-24 08:00 | 1769259600 | 1 | 1 | 2.268 | 146.18 | 122.86 | 7.747
2026-01-24 09:00 | 1769263200 | 1 | 1 | 2.173 | 151.99 | 128.33 | 7.533
2026-01-24 10:00 | 1769266800 | 1 | 1 | 4.048 | 161.21 | 143.07 | 10.761
2026-01-24 12:00 | 1769274000 | 1 | 0.3667 | 0.787 | 164.23 | 119.04 | 5.212
2026-01-24 13:00 | 1769277600 | 1 | 0.3083 | 0.699 | 162.27 | 110.74 | 5.278
2026-01-24 14:00 | 1769281200 | 1 | 0.4361 | 1.093 | 151.77 | 120.22 | 5.054
2026-01-24 15:00 | 1769284800 | 1 | 0.5528 | 1.161 | 157.29 | 119.63 | 6.41
2026-01-24 16:00 | 1769288400 | 1 | 0.5111 | 1.029 | 155.51 | 117.91 | 5.658
2026-01-24 17:00 | 1769292000 | 1 | 0.5583 | 1.081 | 148.74 | 116.56 | 5.09
2026-01-24 18:00 | 1769295600 | 1 | 0.6833 | 1.45 | 145.94 | 118.36 | 5.856
2026-01-24 19:00 | 1769299200 | 1 | 0.7778 | 1.639 | 136.91 | 115.29 | 5.192
2026-01-24 20:00 | 1769302800 | 1 | 1 | 2.259 | 136.19 | 115.73 | 6.775
2026-01-24 21:00 | 1769306400 | 1 | 1 | 2.103 | 152.27 | 128.69 | 7.267
2026-01-24 22:00 | 1769310000 | 1 | 1 | 2.187 | 142.56 | 121.13 | 6.867
2026-01-24 23:00 | 1769313600 | 1 | 1 | 2.162 | 148.28 | 124.62 | 7.498
2026-01-25 00:00 | 1769317200 | 1 | 1 | 2.108 | 155.83 | 131.01 | 7.668
2026-01-25 01:00 | 1769320800 | 1 | 1 | 2.126 | 141.55 | 121.71 | 6.179
2026-01-25 02:00 | 1769324400 | 1 | 1 | 2.26 | 149.18 | 124.71 | 8.101
2026-01-25 03:00 | 1769328000 | 1 | 1 | 2.127 | 153.56 | 129.99 | 7.346
2026-01-25 04:00 | 1769331600 | 1 | 1 | 2.259 | 158.38 | 131.26 | 8.977
2026-01-25 05:00 | 1769335200 | 1 | 1 | 2.118 | 162.31 | 135.48 | 8.327
2026-01-25 06:00 | 1769338800 | 1 | 1 | 2.186 | 167.29 | 137.42 | 9.569
2026-01-25 07:00 | 1769342400 | 1 | 0.975 | 2.15 | 145.27 | 125.13 | 6.345
2026-01-25 08:00 | 1769346000 | 1 | 0.9417 | 2.032 | 146.04 | 123.94 | 6.584
2026-01-25 09:00 | 1769349600 | 1 | 0.7028 | 1.483 | 149.69 | 117.32 | 7.033
2026-01-25 10:00 | 1769353200 | 1 | 0.4167 | 0.787 | 162.31 | 115.8 | 5.366
2026-01-25 11:00 | 1769356800 | 1 | 0.725 | 1.587 | 137.45 | 115.47 | 5.11
2026-01-25 12:00 | 1769360400 | 1 | 1 | 2.141 | 140.39 | 119.66 | 6.504
2026-01-25 13:00 | 1769364000 | 1 | 1 | 2.127 | 157.13 | 130.97 | 8.154
2026-01-25 14:00 | 1769367600 | 1 | 1 | 2.123 | 149.9 | 128.17 | 6.759
2026-01-25 17:00 | 1769378400 | 1 | 0.575 | 1.256 | 158.48 | 125.07 | 6.143
2026-01-25 18:00 | 1769382000 | 1 | 0.8917 | 1.904 | 149.38 | 125.43 | 6.685
2026-01-25 19:00 | 1769385600 | 1 | 0.7444 | 1.6 | 164.24 | 132.81 | 7.365
2026-01-25 20:00 | 1769389200 | 1 | 0.9028 | 1.923 | 158.64 | 132.13 | 7.467
2026-01-25 21:00 | 1769392800 | 1 | 1 | 2.118 | 149.87 | 129.35 | 6.37
2026-01-25 22:00 | 1769396400 | 1 | 1 | 2.124 | 140.16 | 121.53 | 5.801
2026-01-25 23:00 | 1769400000 | 1 | 1 | 2.115 | 159.76 | 133.31 | 8.2
2026-01-26 00:00 | 1769403600 | 1 | 1 | 2.002 | 155.54 | 135.61 | 5.846
2026-01-26 01:00 | 1769407200 | 1 | 1 | 2.13 | 132.86 | 117.07 | 4.931
2026-01-26 02:00 | 1769410800 | 1 | 1 | 2.178 | 140.39 | 119.23 | 6.755
2026-01-26 03:00 | 1769414400 | 1 | 1 | 2.072 | 162.29 | 137.11 | 7.645
2026-01-26 04:00 | 1769418000 | 1 | 0.7806 | 1.678 | 157.08 | 130.55 | 6.523
2026-01-26 05:00 | 1769421600 | 1 | 1 | 2.133 | 127.82 | 113.65 | 4.429
2026-01-26 06:00 | 1769425200 | 1 | 1 | 2.124 | 142.21 | 121.22 | 6.533
2026-01-26 07:00 | 1769428800 | 1 | 1 | 2.129 | 143.96 | 123.91 | 6.253
2026-01-26 08:00 | 1769432400 | 1 | 1 | 2.106 | 160.74 | 134.82 | 7.996
2026-01-26 09:00 | 1769436000 | 1 | 0.9278 | 1.899 | 158.64 | 132.35 | 7.317
2026-01-26 10:00 | 1769439600 | 1 | 0.5639 | 1.227 | 154.84 | 122.3 | 5.853
2026-01-26 11:00 | 1769443200 | 1 | 0.6306 | 1.268 | 137.03 | 117.6 | 3.61
2026-01-26 12:00 | 1769446800 | 1 | 0.9361 | 2.129 | 130.71 | 111.44 | 6.011
2026-01-26 13:00 | 1769450400 | 1 | 0.7778 | 1.668 | 148.69 | 122.24 | 6.465
2026-01-26 15:00 | 1769457600 | 1 | 0.4278 | 0.844 | 148.49 | 116.03 | 4.012
2026-01-26 16:00 | 1769461200 | 1 | 0.625 | 1.229 | 146.57 | 118.36 | 5.079
2026-01-26 17:00 | 1769464800 | 1 | 0.6583 | 1.304 | 152.56 | 123 | 5.647
2026-01-26 18:00 | 1769468400 | 1 | 0.7667 | 1.657 | 146.15 | 122.04 | 5.853
2026-01-26 19:00 | 1769472000 | 1 | 1 | 2.136 | 144.81 | 123.23 | 6.753
2026-01-26 20:00 | 1769475600 | 1 | 1 | 2.127 | 134.29 | 117 | 5.388
2026-01-26 21:00 | 1769479200 | 1 | 1 | 2.113 | 150.53 | 127.4 | 7.161
2026-01-26 22:00 | 1769482800 | 1 | 1 | 2.103 | 153.88 | 132.65 | 6.543
2026-01-26 23:00 | 1769486400 | 1 | 0.7778 | 1.552 | 158.31 | 133.92 | 5.546
2026-01-27 00:00 | 1769490000 | 1 | 0.6306 | 1.298 | 153.1 | 125.92 | 5.166
2026-01-27 01:00 | 1769493600 | 1 | 0.5972 | 1.304 | 154.54 | 124.2 | 5.794
2026-01-27 02:00 | 1769497200 | 1 | 0.6556 | 1.287 | 153.05 | 122.86 | 5.686
2026-01-27 03:00 | 1769500800 | 1 | 0.5889 | 1.177 | 150.52 | 128.43 | 3.809
2026-01-27 04:00 | 1769504400 | 1 | 0.9111 | 1.934 | 136.1 | 117.87 | 5.166
2026-01-27 05:00 | 1769508000 | 1 | 0.7306 | 1.559 | 156.25 | 129.08 | 6.207
2026-01-27 06:00 | 1769511600 | 1 | 0.875 | 1.817 | 140.36 | 121.58 | 5.001
2026-01-27 07:00 | 1769515200 | 1 | 0.6333 | 1.299 | 169.48 | 136.32 | 6.309
2026-01-27 08:00 | 1769518800 | 1 | 0.5694 | 1.11 | 169.39 | 129.17 | 6.536
2026-01-27 09:00 | 1769522400 | 1 | 0.4361 | 0.941 | 166.67 | 123.21 | 5.996
2026-01-27 10:00 | 1769526000 | 1 | 0.3361 | 0.672 | 161.45 | 126.53 | 3.427
2026-01-27 11:00 | 1769529600 | 1 | 0.1917 | 0.351 | 144.28 | 97.66 | 2.393
2026-01-27 12:00 | 1769533200 | 1 | 0.1833 | 0.367 | 156.75 | 105.37 | 2.761
2026-01-27 13:00 | 1769536800 | 1 | 0.4889 | 0.953 | 148.38 | 112.27 | 5.044
2026-01-27 14:00 | 1769540400 | 1 | 0.4472 | 0.857 | 155.52 | 114.11 | 5.199
2026-01-27 15:00 | 1769544000 | 1 | 0.4333 | 0.865 | 151.79 | 122.66 | 3.693
2026-01-27 16:00 | 1769547600 | 1 | 0.5972 | 1.295 | 157.4 | 125.13 | 6.125
2026-01-27 17:00 | 1769551200 | 1 | 0.6806 | 1.315 | 159.44 | 126.83 | 6.283
2026-01-27 18:00 | 1769554800 | 1 | 0.5778 | 1.152 | 156.35 | 123.44 | 5.556
2026-01-27 19:00 | 1769558400 | 1 | 0.3222 | 0.646 | 155.36 | 122.95 | 3.066
2026-01-27 20:00 | 1769562000 | 1 | 0.4694 | 1.055 | 137.89 | 110.62 | 4.2
2026-01-27 21:00 | 1769565600 | 1 | 0.5417 | 1.198 | 159.97 | 124.06 | 6.301
2026-01-27 22:00 | 1769569200 | 1 | 0.5944 | 1.275 | 157.01 | 127.71 | 5.48
2026-01-27 23:00 | 1769572800 | 1 | 0.7806 | 1.559 | 165.77 | 132.21 | 7.663
2026-01-28 01:00 | 1769580000 | 1 | 0.7111 | 1.527 | 157 | 127.51 | 6.598
2026-01-28 02:00 | 1769583600 | 1 | 0.5944 | 1.186 | 168.27 | 131.47 | 6.393
2026-01-28 03:00 | 1769587200 | 1 | 0.6694 | 1.336 | 151.58 | 128.53 | 4.512
2026-01-28 04:00 | 1769590800 | 1 | 0.6889 | 1.489 | 159.16 | 129.85 | 6.396
2026-01-28 05:00 | 1769594400 | 1 | 0.6722 | 1.445 | 166.89 | 132.73 | 7.235
2026-01-28 06:00 | 1769598000 | 1 | 0.7444 | 1.549 | 147.11 | 125.4 | 4.928
2026-01-28 07:00 | 1769601600 | 1 | 0.7722 | 1.588 | 166.52 | 136.49 | 6.99
2026-01-28 08:00 | 1769605200 | 1 | 0.7444 | 1.594 | 164.56 | 133.76 | 7.191
2026-01-28 09:00 | 1769608800 | 1 | 0.6889 | 1.338 | 159.25 | 128.9 | 5.949
2026-01-28 10:00 | 1769612400 | 1 | 0.525 | 1.048 | 158.76 | 129.64 | 4.47
2026-01-28 11:00 | 1769616000 | 1 | 0.3194 | 0.597 | 143.2 | 106.35 | 3.217
2026-01-28 12:00 | 1769619600 | 1 | 0.4667 | 1.055 | 141.63 | 109.26 | 4.996
2026-01-28 13:00 | 1769623200 | 1 | 0.5278 | 1.067 | 151.27 | 122.72 | 4.463
2026-01-28 14:00 | 1769626800 | 1 | 0.5222 | 1.01 | 148.17 | 116.06 | 4.753
2026-01-28 15:00 | 1769630400 | 1 | 0.4361 | 0.986 | 148.73 | 117.32 | 4.537
2026-01-28 16:00 | 1769634000 | 1 | 0.45 | 0.864 | 169.4 | 123.11 | 5.861
2026-01-28 17:00 | 1769637600 | 1 | 0.2444 | 0.489 | 164.16 | 121.03 | 3.089
2026-01-28 18:00 | 1769641200 | 1 | 0.4222 | 0.948 | 164.95 | 121.39 | 6.051
2026-01-28 19:00 | 1769644800 | 1 | 0.6528 | 1.414 | 157.98 | 126.27 | 6.57
2026-01-28 20:00 | 1769648400 | 1 | 0.8694 | 1.845 | 142.23 | 122.12 | 5.436
2026-01-28 21:00 | 1769652000 | 1 | 0.9028 | 1.8 | 160.99 | 136.57 | 6.442
2026-01-28 22:00 | 1769655600 | 1 | 0.7306 | 1.486 | 160.13 | 131.84 | 6.156
2026-01-28 23:00 | 1769659200 | 1 | 0.6861 | 1.48 | 160.9 | 129.63 | 6.78
2026-01-29 00:00 | 1769662800 | 1 | 0.7472 | 1.535 | 150.35 | 127.45 | 5.15
2026-01-29 01:00 | 1769666400 | 1 | 0.7667 | 1.592 | 161.03 | 133.02 | 6.531
2026-01-29 02:00 | 1769670000 | 1 | 0.6167 | 1.334 | 161.64 | 131.58 | 5.876
2026-01-29 03:00 | 1769673600 | 1 | 0.8722 | 1.849 | 143.67 | 121.82 | 5.919
2026-01-29 04:00 | 1769677200 | 1 | 0.7444 | 1.495 | 168.34 | 139.39 | 6.342
2026-01-29 05:00 | 1769680800 | 1 | 0.5528 | 1.199 | 163.85 | 131.11 | 5.747
2026-01-29 06:00 | 1769684400 | 1 | 0.9778 | 1.918 | 144.85 | 123.08 | 6.12
2026-01-29 07:00 | 1769688000 | 1 | 0.8528 | 1.671 | 168.23 | 136.91 | 7.668
2026-01-29 08:00 | 1769691600 | 1 | 0.5472 | 1.089 | 166.5 | 134.37 | 5.127
2026-01-29 09:00 | 1769695200 | 1 | 0.6528 | 1.312 | 160.85 | 130 | 5.932
2026-01-29 10:00 | 1769698800 | 1 | 0.5639 | 1.184 | 160.48 | 125.42 | 6.085
2026-01-29 11:00 | 1769702400 | 1 | 0.2167 | 0.433 | 154.43 | 112.9 | 2.636
2026-01-29 12:00 | 1769706000 | 1 | 0.3667 | 0.694 | 144.22 | 107.84 | 3.702
2026-01-29 13:00 | 1769709600 | 1 | 0.4111 | 0.858 | 155.46 | 116.15 | 4.94
2026-01-29 14:00 | 1769713200 | 1 | 0.3056 | 0.572 | 144.7 | 105.43 | 3.286
2026-01-29 15:00 | 1769716800 | 1 | 0.5833 | 1.171 | 140.75 | 115.75 | 4.288
2026-01-29 16:00 | 1769720400 | 1 | 0.75 | 1.454 | 151.63 | 125.81 | 5.502
2026-01-29 17:00 | 1769724000 | 1 | 0.7333 | 1.446 | 171.55 | 134.71 | 7.797
2026-01-29 18:00 | 1769727600 | 1 | 0.6556 | 1.265 | 162 | 129.39 | 6.045
2026-01-29 19:00 | 1769731200 | 1 | 0.7111 | 1.416 | 159.35 | 133.14 | 5.438
2026-01-29 20:00 | 1769734800 | 1 | 0.875 | 1.856 | 148.67 | 126.32 | 6.076
2026-01-29 21:00 | 1769738400 | 1 | 0.8639 | 1.832 | 159.36 | 133.21 | 7.019
2026-01-29 22:00 | 1769742000 | 1 | 0.8583 | 1.824 | 153.06 | 128.37 | 6.599
2026-01-29 23:00 | 1769745600 | 1 | 0.75 | 1.497 | 164.53 | 135.41 | 6.382
2026-01-30 00:00 | 1769749200 | 1 | 0.8306 | 1.701 | 156.86 | 131.87 | 6.23
2026-01-30 01:00 | 1769752800 | 1 | 0.6861 | 1.472 | 165.38 | 133.37 | 6.906
2026-01-30 02:00 | 1769756400 | 1 | 0.8806 | 1.868 | 146.52 | 125.64 | 5.713
2026-01-30 03:00 | 1769760000 | 1 | 0.9056 | 1.91 | 158.78 | 133.49 | 7.08
2026-01-30 04:00 | 1769763600 | 1 | 0.8806 | 1.873 | 158.05 | 132.93 | 6.893
2026-01-30 05:00 | 1769767200 | 1 | 1 | 2.031 | 148.49 | 129.27 | 5.719
2026-01-30 06:00 | 1769770800 | 1 | 0.9806 | 2.042 | 163.74 | 138.41 | 7.58
2026-01-30 07:00 | 1769774400 | 1 | 0.8278 | 1.74 | 167.11 | 136.63 | 7.772
2026-01-30 08:00 | 1769778000 | 1 | 0.7917 | 1.618 | 169.82 | 137.77 | 7.601
2026-01-30 09:00 | 1769781600 | 1 | 0.5889 | 1.28 | 165.33 | 132.05 | 6.244
2026-01-30 11:00 | 1769788800 | 1 | 0.45 | 0.857 | 158.26 | 121.81 | 4.564
2026-01-30 12:00 | 1769792400 | 1 | 0.6361 | 1.239 | 144.38 | 116.02 | 5.14
2026-01-30 13:00 | 1769796000 | 1 | 0.6889 | 1.337 | 151.75 | 122.41 | 5.746
2026-01-30 14:00 | 1769799600 | 1 | 0.7583 | 1.635 | 150.04 | 124.8 | 6.047
2026-01-30 15:00 | 1769803200 | 1 | 0.775 | 1.666 | 147.61 | 124.65 | 5.601
2026-01-30 16:00 | 1769806800 | 1 | 0.7333 | 1.568 | 165.56 | 132.97 | 7.49
2026-01-30 17:00 | 1769810400 | 1 | 0.4861 | 0.972 | 157.34 | 126.53 | 4.385
2026-01-30 18:00 | 1769814000 | 1 | 0.5472 | 1.065 | 156.03 | 121.39 | 5.406
2026-01-30 19:00 | 1769817600 | 1 | 0.5278 | 1.137 | 155.71 | 122.91 | 5.465
2026-01-30 20:00 | 1769821200 | 1 | 1 | 2.119 | 138.47 | 119.86 | 5.778
2026-01-30 21:00 | 1769824800 | 1 | 1 | 2.117 | 154.28 | 130.6 | 7.346
2026-01-30 22:00 | 1769828400 | 1 | 1 | 2.139 | 169.7 | 141.21 | 8.93
2026-01-30 23:00 | 1769832000 | 0.95 | 1 | 2.113 | 150.33 | 131.05 | 5.671
2026-01-31 00:00 | 1769835600 | 1 | 1 | 2.103 | 163.16 | 137.41 | 7.932
2026-01-31 01:00 | 1769839200 | 1 | 1 | 2.12 | 146.63 | 127.05 | 6.082
2026-01-31 02:00 | 1769842800 | 1 | 1 | 2.207 | 164.39 | 135.89 | 9.216
2026-01-31 03:00 | 1769846400 | 1 | 1 | 2.113 | 151.79 | 130.99 | 6.439
2026-01-31 04:00 | 1769850000 | 1 | 1 | 2.107 | 157.71 | 132.96 | 7.639
2026-01-31 05:00 | 1769853600 | 1 | 1 | 2.098 | 166.24 | 140.28 | 7.979
2026-01-31 06:00 | 1769857200 | 1 | 1 | 2.108 | 151.35 | 129.44 | 6.768
2026-01-31 07:00 | 1769860800 | 1 | 1 | 2.102 | 159.06 | 135.8 | 7.168
2026-01-31 08:00 | 1769864400 | 1 | 1 | 2.109 | 146.65 | 125.43 | 6.556
2026-01-31 09:00 | 1769868000 | 1 | 1 | 2.106 | 154.2 | 132.37 | 6.737
2026-01-31 10:00 | 1769871600 | 1 | 0.9806 | 2.074 | 148.83 | 126.48 | 6.793
2026-01-31 11:00 | 1769875200 | 1 | 0.4472 | 0.855 | 153.4 | 117.59 | 4.478
2026-01-31 12:00 | 1769878800 | 1 | 0.2556 | 0.469 | 147.24 | 104.76 | 2.915
2026-01-31 13:00 | 1769882400 | 1 | 0.3472 | 0.74 | 131.84 | 101.36 | 3.3
2026-01-31 14:00 | 1769886000 | 1 | 0.525 | 1.076 | 137.74 | 107 | 4.843
2026-01-31 15:00 | 1769889600 | 1 | 0.6722 | 1.468 | 141.12 | 118.28 | 4.91
2026-01-31 16:00 | 1769893200 | 1 | 0.8972 | 1.911 | 141.45 | 120.25 | 5.923
2026-01-31 17:00 | 1769896800 | 1 | 1 | 2.125 | 154.2 | 131.2 | 7.162
2026-01-31 18:00 | 1769900400 | 1 | 0.7806 | 1.645 | 143.92 | 120.99 | 5.526
2026-01-31 19:00 | 1769904000 | 1 | 0.4583 | 0.941 | 163.42 | 124.73 | 5.334
2026-01-31 20:00 | 1769907600 | 1 | 0.3167 | 0.602 | 155.14 | 110.95 | 3.884
2026-01-31 21:00 | 1769911200 | 1 | 0.4972 | 1.126 | 139.33 | 109.49 | 4.921
2026-01-31 22:00 | 1769914800 | 1 | 0.8361 | 1.78 | 152.89 | 127.27 | 6.682
2026-01-31 23:00 | 1769918400 | 1 | 0.6694 | 1.45 | 165.83 | 132.42 | 7.099
2026-02-01 00:00 | 1769922000 | 1 | 0.8694 | 1.858 | 145.74 | 125.17 | 5.601
2026-02-01 01:00 | 1769925600 | 1 | 0.9111 | 1.928 | 150.45 | 127.23 | 6.558
2026-02-01 02:00 | 1769929200 | 1 | 0.7667 | 1.647 | 163.89 | 134.84 | 7.012
2026-02-01 03:00 | 1769932800 | 1 | 0.8722 | 1.861 | 151.71 | 128.06 | 6.449
2026-02-01 04:00 | 1769936400 | 1 | 0.8083 | 1.731 | 157.52 | 132.11 | 6.445
2026-02-01 05:00 | 1769940000 | 1 | 0.7889 | 1.554 | 168.06 | 134.91 | 7.549
2026-02-01 06:00 | 1769943600 | 1 | 0.6667 | 1.374 | 167.47 | 134.69 | 6.597
2026-02-01 07:00 | 1769947200 | 1 | 0.9306 | 1.98 | 141.64 | 121.84 | 5.745
2026-02-01 08:00 | 1769950800 | 1 | 0.9528 | 1.924 | 157.12 | 132.05 | 7.069
2026-02-01 09:00 | 1769954400 | 1 | 0.7667 | 1.659 | 137.3 | 117.28 | 4.867
2026-02-01 10:00 | 1769958000 | 1 | 0.5861 | 1.136 | 153.14 | 124.24 | 4.809
2026-02-01 11:00 | 1769961600 | 1 | 0.4889 | 0.94 | 148.92 | 113.12 | 4.92
2026-02-01 12:00 | 1769965200 | 1 | 0.325 | 0.77 | 132.91 | 106.24 | 3.008
2026-02-01 13:00 | 1769968800 | 1 | 0.3889 | 0.806 | 141.95 | 105.67 | 4.276
2026-02-01 14:00 | 1769972400 | 1 | 0.4611 | 1.046 | 139.95 | 113.01 | 4.131
2026-02-01 15:00 | 1769976000 | 1 | 0.875 | 1.871 | 138.04 | 116.34 | 5.952
2026-02-01 16:00 | 1769979600 | 1 | 0.6667 | 1.449 | 154.57 | 126.94 | 5.866
2026-02-01 17:00 | 1769983200 | 1 | 0.65 | 1.415 | 138.64 | 115.11 | 4.88
2026-02-01 18:00 | 1769986800 | 1 | 0.5333 | 1.036 | 150.76 | 117.67 | 5.017
2026-02-01 19:00 | 1769990400 | 1 | 0.4972 | 0.952 | 136.45 | 111.58 | 3.466
2026-02-01 20:00 | 1769994000 | 1 | 0.7556 | 1.487 | 142.9 | 117.07 | 5.627
2026-02-01 21:00 | 1769997600 | 1 | 0.55 | 1.208 | 159.06 | 124.79 | 6.069
2026-02-01 22:00 | 1770001200 | 1 | 0.6972 | 1.532 | 139.08 | 117.39 | 4.865
2026-02-01 23:00 | 1770004800 | 1 | 0.6833 | 1.492 | 156.14 | 128.94 | 5.942
2026-02-02 00:00 | 1770008400 | 1 | 0.7444 | 1.544 | 147.87 | 124 | 5.404
2026-02-02 01:00 | 1770012000 | 1 | 0.7194 | 1.485 | 160.55 | 129.94 | 6.66
2026-02-02 02:00 | 1770015600 | 1 | 0.5278 | 1.175 | 149.4 | 122.22 | 4.678
2026-02-02 03:00 | 1770019200 | 1 | 0.7722 | 1.595 | 150.12 | 124.72 | 5.936
2026-02-02 04:00 | 1770022800 | 1 | 0.8083 | 1.573 | 153.05 | 126.32 | 6.157
2026-02-02 05:00 | 1770026400 | 1 | 0.7611 | 1.651 | 143.34 | 121.19 | 5.357
2026-02-02 06:00 | 1770030000 | 1 | 0.7444 | 1.644 | 153.23 | 126.23 | 6.5
2026-02-02 07:00 | 1770033600 | 1 | 0.5722 | 1.182 | 165.33 | 128.15 | 6.438
2026-02-02 08:00 | 1770037200 | 1 | 0.4361 | 0.872 | 165.93 | 128.21 | 4.816
2026-02-02 09:00 | 1770040800 | 1 | 0.4806 | 0.928 | 164.81 | 121.96 | 5.817
2026-02-02 10:00 | 1770044400 | 1 | 0.3861 | 0.729 | 150.5 | 116.6 | 3.622
2026-02-02 11:00 | 1770048000 | 1 | 0.2778 | 0.522 | 126.99 | 94.65 | 2.458
2026-02-02 12:00 | 1770051600 | 1 | 0.2889 | 0.537 | 124.64 | 94.02 | 2.408
2026-02-02 13:00 | 1770055200 | 1 | 0.1806 | 0.316 | 134.32 | 89.81 | 2.06
2026-02-02 14:00 | 1770058800 | 1 | 0.2806 | 0.523 | 134.03 | 94.59 | 3.025
2026-02-02 15:00 | 1770062400 | 1 | 0.3417 | 0.653 | 133.21 | 103.77 | 2.818
2026-02-02 16:00 | 1770066000 | 1 | 0.55 | 1.084 | 151.03 | 120.94 | 4.779
2026-02-02 17:00 | 1770069600 | 1 | 0.5972 | 1.17 | 141.79 | 115.17 | 4.56
2026-02-02 18:00 | 1770073200 | 1 | 0.4944 | 1.102 | 139.46 | 112.86 | 4.297
2026-02-02 19:00 | 1770076800 | 1 | 0.4917 | 0.955 | 140.28 | 113.17 | 3.781
2026-02-02 20:00 | 1770080400 | 1 | 0.4528 | 0.877 | 140.77 | 106.3 | 4.421
2026-02-02 21:00 | 1770084000 | 1 | 0.4167 | 0.812 | 149.84 | 117.69 | 3.811
2026-02-02 22:00 | 1770087600 | 1 | 0.5972 | 1.19 | 146.89 | 120.28 | 4.642
2026-02-02 23:00 | 1770091200 | 1 | 0.5667 | 1.159 | 146.53 | 118.18 | 4.815
2026-02-03 00:00 | 1770094800 | 1 | 0.5444 | 1.051 | 151.74 | 121.86 | 4.601
2026-02-03 01:00 | 1770098400 | 1 | 0.5778 | 1.248 | 150.09 | 120.65 | 5.384
2026-02-03 02:00 | 1770102000 | 1 | 0.6361 | 1.382 | 142.28 | 117.53 | 4.997
2026-02-03 03:00 | 1770105600 | 1 | 0.5778 | 1.195 | 152.2 | 121.79 | 5.324
2026-02-03 04:00 | 1770109200 | 1 | 0.5306 | 1.038 | 159.3 | 124.92 | 5.226
2026-02-03 05:00 | 1770112800 | 0.95 | 0.5965 | 1.317 | 137.16 | 113.76 | 4.291
2026-02-03 06:00 | 1770116400 | 1 | 0.6194 | 1.298 | 154.31 | 124.94 | 5.587
2026-02-03 08:00 | 1770123600 | 1 | 0.4194 | 0.781 | 152.27 | 115.59 | 4.192
2026-02-03 09:00 | 1770127200 | 1 | 0.3806 | 0.762 | 165.54 | 126.61 | 4.346
2026-02-03 10:00 | 1770130800 | 1 | 0.3 | 0.564 | 163.33 | 112.96 | 4.146
2026-02-03 11:00 | 1770134400 | 1 | 0.1667 | 0.289 | 159.85 | 95.26 | 2.74
2026-02-03 12:00 | 1770138000 | 1 | 0.0944 | 0.193 | 151.14 | 97.05 | 1.519
2026-02-03 13:00 | 1770141600 | 1 | 0.2083 | 0.517 | 147.62 | 99.71 | 3.628
2026-02-03 14:00 | 1770145200 | 1 | 0.2361 | 0.529 | 129.91 | 95.64 | 2.648
2026-02-03 15:00 | 1770148800 | 1 | 0.3472 | 0.705 | 133.86 | 105.81 | 2.896
2026-02-03 16:00 | 1770152400 | 1 | 0.5528 | 1.128 | 136.1 | 112.77 | 3.852
2026-02-03 17:00 | 1770156000 | 1 | 0.4833 | 0.971 | 146.77 | 117.85 | 4.115
2026-02-03 18:00 | 1770159600 | 1 | 0.2833 | 0.57 | 138.21 | 108.99 | 2.441
2026-02-03 19:00 | 1770163200 | 1 | 0.4667 | 0.98 | 142.18 | 109.21 | 4.739
2026-02-03 20:00 | 1770166800 | 1 | 0.2444 | 0.493 | 143.86 | 109.47 | 2.486
2026-02-03 21:00 | 1770170400 | 1 | 0.4833 | 1.017 | 138.4 | 109.28 | 4.342
2026-02-03 22:00 | 1770174000 | 1 | 0.4889 | 0.993 | 156.42 | 128.69 | 4.029
2026-02-03 23:00 | 1770177600 | 1 | 0.625 | 1.35 | 149.63 | 121.42 | 5.574
2026-02-04 01:00 | 1770184800 | 1 | 0.4667 | 1.031 | 159.42 | 123.6 | 5.41
2026-02-04 02:00 | 1770188400 | 1 | 0.6028 | 1.288 | 141.7 | 119.91 | 4.111
2026-02-04 03:00 | 1770192000 | 1 | 0.7028 | 1.415 | 152.47 | 128.11 | 5.048
2026-02-04 04:00 | 1770195600 | 1 | 0.7722 | 1.528 | 155.56 | 127.09 | 6.372
2026-02-04 05:00 | 1770199200 | 1 | 0.7361 | 1.517 | 139.85 | 119.74 | 4.471
2026-02-04 06:00 | 1770202800 | 1 | 0.7444 | 1.555 | 150.87 | 127.53 | 5.318
2026-02-04 07:00 | 1770206400 | 1 | 0.6083 | 1.18 | 159.03 | 125.52 | 5.796
2026-02-04 08:00 | 1770210000 | 1 | 0.3861 | 0.77 | 165.13 | 126.78 | 4.327
2026-02-04 09:00 | 1770213600 | 1 | 0.4694 | 0.903 | 136.23 | 108.99 | 3.601
2026-02-04 10:00 | 1770217200 | 1 | 0.6583 | 1.327 | 146.37 | 122.15 | 4.713
2026-02-04 11:00 | 1770220800 | 1 | 0.4528 | 1.055 | 160.79 | 116.37 | 6.867
2026-02-04 13:00 | 1770228000 | 1 | 0.5278 | 1.065 | 133.81 | 110.7 | 3.604
2026-02-04 14:00 | 1770231600 | 1 | 0.4417 | 0.851 | 138.55 | 107.07 | 3.927
2026-02-04 15:00 | 1770235200 | 1 | 0.45 | 0.976 | 127.61 | 108.08 | 2.79
2026-02-04 16:00 | 1770238800 | 1 | 0.65 | 1.334 | 143.68 | 119.93 | 4.641
2026-02-04 17:00 | 1770242400 | 1 | 0.6694 | 1.329 | 140.91 | 116.46 | 4.764
2026-02-04 18:00 | 1770246000 | 1 | 0.6222 | 1.209 | 139.31 | 115.52 | 4.212
2026-02-04 19:00 | 1770249600 | 1 | 0.7444 | 1.507 | 128.16 | 113.48 | 3.24
2026-02-04 20:00 | 1770253200 | 1 | 1 | 2.112 | 135.02 | 117.23 | 5.506
2026-02-04 22:00 | 1770260400 | 1 | 0.6167 | 1.225 | 149.74 | 123.21 | 4.762
2026-02-04 23:00 | 1770264000 | 1 | 0.4972 | 1.037 | 150.07 | 119.9 | 4.584
2026-02-05 00:00 | 1770267600 | 1 | 0.5167 | 1.039 | 147.46 | 122.95 | 3.729
2026-02-05 01:00 | 1770271200 | 1 | 0.5944 | 1.289 | 148.29 | 120.39 | 5.271
2026-02-05 02:00 | 1770274800 | 1 | 0.5917 | 1.186 | 138.52 | 118.02 | 3.562
2026-02-05 03:00 | 1770278400 | 1 | 0.675 | 1.448 | 153.79 | 126.3 | 5.829
2026-02-05 04:00 | 1770282000 | 1 | 0.5778 | 1.16 | 150.55 | 120.47 | 5.109
2026-02-05 05:00 | 1770285600 | 1 | 0.5111 | 1.029 | 146.35 | 120.84 | 3.841
2026-02-05 06:00 | 1770289200 | 1 | 0.5583 | 1.096 | 151.63 | 122.34 | 4.704
2026-02-05 09:00 | 1770300000 | 1 | 0.2389 | 0.482 | 157.87 | 118.45 | 2.78
2026-02-05 10:00 | 1770303600 | 1 | 0.25 | 0.575 | 151.2 | 107.7 | 3.66
2026-02-05 11:00 | 1770307200 | 1 | 0.3194 | 0.647 | 138.59 | 103.25 | 3.345
2026-02-05 12:00 | 1770310800 | 1 | 0.4083 | 0.783 | 142.41 | 110.68 | 3.64
2026-02-05 13:00 | 1770314400 | 1 | 0.4083 | 0.821 | 140.95 | 113.52 | 3.3
2026-02-05 14:00 | 1770318000 | 1 | 0.3528 | 0.673 | 138 | 107.28 | 3.029
2026-02-05 15:00 | 1770321600 | 1 | 0.5528 | 1.216 | 127.89 | 105.55 | 3.978
2026-02-05 16:00 | 1770325200 | 1 | 0.4833 | 0.969 | 159.28 | 126.7 | 4.623
2026-02-05 17:00 | 1770328800 | 1 | 0.5111 | 1.045 | 154.05 | 123 | 4.755
2026-02-05 18:00 | 1770332400 | 1 | 0.5583 | 1.116 | 153.49 | 125.48 | 4.583
2026-02-05 19:00 | 1770336000 | 1 | 0.6306 | 1.369 | 143.3 | 118.13 | 5.05
2026-02-05 20:00 | 1770339600 | 0.9528 | 0.8921 | 1.831 | 132.14 | 115.06 | 4.364
2026-02-05 21:00 | 1770343200 | 1 | 0.5028 | 0.975 | 161.22 | 124.8 | 5.197
2026-02-05 22:00 | 1770346800 | 1 | 0.5167 | 1.036 | 160.39 | 127 | 5.071
2026-02-05 23:00 | 1770350400 | 1 | 0.5833 | 1.278 | 150.42 | 121.71 | 5.374
2026-02-06 00:00 | 1770354000 | 1 | 0.6694 | 1.333 | 166.77 | 136.95 | 5.822
2026-02-06 01:00 | 1770357600 | 1 | 0.6167 | 1.207 | 159.59 | 127.62 | 5.648
2026-02-06 02:00 | 1770361200 | 1 | 0.6361 | 1.371 | 159.98 | 130.04 | 6.015
2026-02-06 03:00 | 1770364800 | 1 | 0.7167 | 1.442 | 151.43 | 129.98 | 4.528
2026-02-06 05:00 | 1770372000 | 1 | 0.8389 | 1.785 | 156.4 | 131.78 | 6.439
2026-02-06 06:00 | 1770375600 | 1 | 0.7528 | 1.609 | 167.55 | 136.75 | 7.256
2026-02-06 07:00 | 1770379200 | 1 | 0.7278 | 1.453 | 167.81 | 137.14 | 6.531
2026-02-06 08:00 | 1770382800 | 1 | 0.7694 | 1.584 | 167.68 | 135.96 | 7.357
2026-02-06 09:00 | 1770386400 | 1 | 0.7 | 1.493 | 158.97 | 130.24 | 6.275
2026-02-06 10:00 | 1770390000 | 1 | 0.6222 | 1.246 | 153.19 | 127.92 | 4.613
2026-02-06 11:00 | 1770393600 | 1 | 0.6194 | 1.204 | 146.32 | 119.28 | 4.771
2026-02-06 12:00 | 1770397200 | 1 | 0.5778 | 1.16 | 145.37 | 121.11 | 4.123
2026-02-06 13:00 | 1770400800 | 1 | 0.5861 | 1.138 | 146.64 | 118.7 | 4.651
2026-02-06 14:00 | 1770404400 | 1 | 0.4833 | 0.976 | 138.82 | 115.68 | 3.304
2026-02-06 15:00 | 1770408000 | 1 | 0.5917 | 1.283 | 151.73 | 123.74 | 5.263
2026-02-06 16:00 | 1770411600 | 1 | 0.7194 | 1.434 | 155.74 | 128.59 | 5.704
2026-02-06 17:00 | 1770415200 | 1 | 0.5694 | 1.231 | 157.14 | 126.06 | 5.593
2026-02-06 18:00 | 1770418800 | 1 | 0.675 | 1.35 | 152.22 | 128.48 | 4.696
2026-02-06 19:00 | 1770422400 | 1 | 0.7556 | 1.601 | 143.38 | 120.82 | 5.291
2026-02-06 20:00 | 1770426000 | 1 | 0.9139 | 1.94 | 130.04 | 113.57 | 4.68
2026-02-06 21:00 | 1770429600 | 1 | 1 | 2.104 | 152.58 | 130.03 | 6.953
2026-02-06 22:00 | 1770433200 | 1 | 1 | 2.042 | 150.49 | 130.29 | 6.046
2026-02-06 23:00 | 1770436800 | 1 | 1 | 2.056 | 158.88 | 136.02 | 6.886
2026-02-07 00:00 | 1770440400 | 1 | 0.9389 | 1.91 | 156.98 | 133.73 | 6.508
2026-02-07 01:00 | 1770444000 | 1 | 0.9 | 1.808 | 154.95 | 132.35 | 5.986
2026-02-07 02:00 | 1770447600 | 1 | 0.8861 | 1.861 | 154.7 | 131.7 | 6.272
2026-02-07 03:00 | 1770451200 | 0.9528 | 1 | 2.003 | 145.74 | 126.42 | 5.403
2026-02-07 04:00 | 1770454800 | 1 | 0.9028 | 1.894 | 162.15 | 135.96 | 7.27
2026-02-07 05:00 | 1770458400 | 0.9528 | 1 | 2.004 | 149.79 | 131.03 | 5.25
2026-02-07 06:00 | 1770462000 | 1 | 0.9 | 1.903 | 157.05 | 132.43 | 6.865
2026-02-07 07:00 | 1770465600 | 1 | 1 | 2.1 | 139.58 | 122.21 | 5.346
2026-02-07 08:00 | 1770469200 | 1 | 1 | 2 | 151.21 | 132.02 | 5.625
2026-02-07 09:00 | 1770472800 | 1 | 1 | 2.109 | 133.31 | 118.56 | 4.557
2026-02-07 10:00 | 1770476400 | 1 | 0.8944 | 1.793 | 144.19 | 125.04 | 5.032
2026-02-07 11:00 | 1770480000 | 1 | 0.5583 | 1.217 | 147.31 | 118.8 | 5.083
2026-02-07 12:00 | 1770483600 | 1 | 0.2556 | 0.514 | 132.59 | 106.19 | 1.987
2026-02-07 13:00 | 1770487200 | 1 | 0.4722 | 0.908 | 125.73 | 101.24 | 3.257
2026-02-07 14:00 | 1770490800 | 1 | 0.4917 | 0.952 | 143.04 | 111.13 | 4.45
2026-02-07 15:00 | 1770494400 | 1 | 0.45 | 0.902 | 141.88 | 117.58 | 3.21
2026-02-07 16:00 | 1770498000 | 1 | 0.7806 | 1.676 | 133.29 | 113.93 | 4.757
2026-02-07 17:00 | 1770501600 | 1 | 0.6889 | 1.482 | 145.51 | 120.69 | 5.391
2026-02-07 18:00 | 1770505200 | 1 | 0.8139 | 1.634 | 139.12 | 121.27 | 4.273
2026-02-07 19:00 | 1770508800 | 1 | 0.6417 | 1.388 | 146.56 | 120.02 | 5.397
2026-02-07 20:00 | 1770512400 | 1 | 0.725 | 1.557 | 135.15 | 114.34 | 4.749
2026-02-07 21:00 | 1770516000 | 1 | 0.6111 | 1.225 | 148.23 | 125.82 | 4.023
2026-02-07 22:00 | 1770519600 | 1 | 0.7556 | 1.616 | 140.53 | 118.58 | 5.19
2026-02-07 23:00 | 1770523200 | 1 | 0.7167 | 1.517 | 151.89 | 126.28 | 5.693
2026-02-08 00:00 | 1770526800 | 1 | 0.7194 | 1.448 | 143.63 | 122.94 | 4.389
2026-02-08 01:00 | 1770530400 | 1 | 0.6278 | 1.36 | 154.03 | 124.93 | 5.799
2026-02-08 02:00 | 1770534000 | 1 | 0.7056 | 1.415 | 148.53 | 127.61 | 4.334
2026-02-08 03:00 | 1770537600 | 1 | 0.8306 | 1.699 | 146.86 | 123.67 | 5.773
2026-02-08 04:00 | 1770541200 | 1 | 0.8722 | 1.841 | 151.76 | 128.54 | 6.264
2026-02-08 05:00 | 1770544800 | 1 | 1 | 2.007 | 146 | 126.96 | 5.601
2026-02-08 06:00 | 1770548400 | 1 | 0.9028 | 1.904 | 157.59 | 133.06 | 6.846
2026-02-08 08:00 | 1770555600 | 1 | 0.8972 | 1.825 | 158.58 | 135.18 | 6.257
2026-02-08 10:00 | 1770562800 | 1 | 0.8528 | 1.732 | 148.84 | 124.94 | 6.066
2026-02-08 11:00 | 1770566400 | 1 | 0.2556 | 0.513 | 148.54 | 115.87 | 2.455
2026-02-08 12:00 | 1770570000 | 1 | 0.2667 | 0.532 | 146.09 | 102.37 | 3.409
2026-02-08 13:00 | 1770573600 | 1 | 0.2972 | 0.597 | 130.18 | 99.18 | 2.709
2026-02-08 14:00 | 1770577200 | 1 | 0.3528 | 0.724 | 142.28 | 105.49 | 3.903
2026-02-08 15:00 | 1770580800 | 1 | 0.4167 | 0.837 | 139.66 | 110.28 | 3.603
2026-02-08 16:00 | 1770584400 | 1 | 0.7222 | 1.564 | 129.87 | 108.95 | 4.794
2026-02-08 17:00 | 1770588000 | 1 | 0.6139 | 1.3 | 153.63 | 120.63 | 6.28
2026-02-08 18:00 | 1770591600 | 1 | 0.6028 | 1.223 | 145.31 | 122.74 | 4.044
2026-02-08 19:00 | 1770595200 | 1 | 0.7111 | 1.457 | 148.64 | 117.45 | 6.661
2026-02-08 20:00 | 1770598800 | 1 | 0.425 | 0.863 | 148.92 | 116.81 | 4.051
2026-02-08 21:00 | 1770602400 | 0.9528 | 0.7347 | 1.594 | 144.42 | 116.71 | 6.164
2026-02-08 23:00 | 1770609600 | 1 | 1 | 2.116 | 152.42 | 129.18 | 7.207
2026-02-09 00:00 | 1770613200 | 1 | 1 | 2.015 | 146.88 | 127.96 | 5.587
2026-02-09 01:00 | 1770616800 | 1 | 1 | 2.114 | 157.82 | 132.2 | 7.934
2026-02-09 02:00 | 1770620400 | 1 | 1 | 2.113 | 151.31 | 129.35 | 6.8
2026-02-09 03:00 | 1770624000 | 1 | 1 | 2.104 | 165.17 | 136.77 | 8.755
2026-02-09 04:00 | 1770627600 | 1 | 1 | 2.006 | 157.33 | 136.52 | 6.116
2026-02-09 06:00 | 1770634800 | 1 | 1 | 2.113 | 153.37 | 129.31 | 7.451
2026-02-09 07:00 | 1770638400 | 1 | 1 | 2.115 | 156.86 | 131.88 | 7.741
2026-02-09 08:00 | 1770642000 | 1 | 1 | 1.998 | 168.16 | 142.56 | 7.496
2026-02-09 09:00 | 1770645600 | 1 | 0.8611 | 1.68 | 161.65 | 133.1 | 7.029
2026-02-09 10:00 | 1770649200 | 1 | 0.6917 | 1.398 | 146.66 | 123.63 | 4.719
2026-02-09 11:00 | 1770652800 | 1 | 0.2722 | 0.645 | 136.33 | 104.54 | 2.999
2026-02-09 12:00 | 1770656400 | 1 | 0.4667 | 0.945 | 134.67 | 107.79 | 3.723
2026-02-09 13:00 | 1770660000 | 1 | 0.4583 | 1.018 | 146.21 | 112.56 | 5.021
2026-02-09 14:00 | 1770663600 | 1 | 0.2389 | 0.486 | 136.04 | 106.48 | 2.103
2026-02-09 15:00 | 1770667200 | 1 | 0.5833 | 1.262 | 133.64 | 107.96 | 4.748
2026-02-09 16:00 | 1770670800 | 1 | 0.7472 | 1.511 | 143.72 | 118.44 | 5.601
2026-02-09 17:00 | 1770674400 | 1 | 0.6306 | 1.326 | 155.81 | 124.11 | 6.154
2026-02-09 18:00 | 1770678000 | 1 | 0.6167 | 1.246 | 150.77 | 123.13 | 5.044
2026-02-09 19:00 | 1770681600 | 1 | 0.4639 | 0.943 | 147.03 | 113.43 | 4.629
2026-02-09 20:00 | 1770685200 | 0.9528 | 0.656 | 1.326 | 144.21 | 116.51 | 5.128
2026-02-09 21:00 | 1770688800 | 1 | 0.6556 | 1.424 | 149.44 | 120.4 | 6.06
2026-02-09 22:00 | 1770692400 | 1 | 0.5889 | 1.289 | 144.1 | 117.27 | 5.066
2026-02-09 23:00 | 1770696000 | 1 | 0.6278 | 1.264 | 156.1 | 126.88 | 5.411
2026-02-10 00:00 | 1770699600 | 1 | 0.6917 | 1.394 | 148.26 | 120.25 | 5.721
2026-02-10 01:00 | 1770703200 | 1 | 0.5833 | 1.229 | 160.2 | 127.28 | 5.929
2026-02-10 02:00 | 1770706800 | 1 | 0.6639 | 1.451 | 143.14 | 118.61 | 5.212
2026-02-10 03:00 | 1770710400 | 1 | 0.7917 | 1.594 | 148.47 | 126.37 | 5.163
2026-02-10 04:00 | 1770714000 | 1 | 0.8917 | 1.868 | 143.9 | 121.44 | 6.148
2026-02-10 05:00 | 1770717600 | 1 | 0.85 | 1.668 | 157.44 | 128.82 | 6.998
2026-02-10 07:00 | 1770724800 | 1 | 0.5361 | 1.074 | 168.99 | 129.95 | 6.138
2026-02-10 08:00 | 1770728400 | 1 | 0.3333 | 0.644 | 165.48 | 117.88 | 4.489
2026-02-10 09:00 | 1770732000 | 1 | 0.3861 | 0.746 | 163.78 | 110.91 | 5.779
2026-02-10 10:00 | 1770735600 | 1 | 0.1472 | 0.296 | 162.82 | 113.71 | 2.129
2026-02-10 11:00 | 1770739200 | 1 | 0.0833 | 0.263 | 156.7 | 85.1 | 2.749
2026-02-10 12:00 | 1770742800 | 1 | 0.0889 | 0.179 | 144.85 | 90.34 | 1.431
2026-02-10 13:00 | 1770746400 | 1 | 0.2 | 0.404 | 133.93 | 95.17 | 2.294
2026-02-10 14:00 | 1770750000 | 1 | 0.2167 | 0.439 | 120.01 | 93.16 | 1.727
2026-02-10 15:00 | 1770753600 | 1 | 0.3889 | 0.747 | 137.02 | 101.01 | 3.943
2026-02-10 16:00 | 1770757200 | 1 | 0.4917 | 0.995 | 134.96 | 112.59 | 3.259
2026-02-10 17:00 | 1770760800 | 1 | 0.5694 | 1.237 | 142.33 | 114.37 | 5.07
2026-02-10 18:00 | 1770764400 | 1 | 0.4528 | 0.915 | 140.23 | 112.83 | 3.674
2026-02-10 19:00 | 1770768000 | 1 | 0.4667 | 1.027 | 138.45 | 110.02 | 4.279
2026-02-10 20:00 | 1770771600 | 1 | 0.5667 | 1.15 | 134.39 | 112.68 | 3.657
2026-02-10 21:00 | 1770775200 | 1 | 0.7694 | 1.579 | 140.64 | 117.56 | 5.335
2026-02-10 22:00 | 1770778800 | 0.95 | 0.6199 | 1.248 | 146.76 | 121.48 | 4.39
2026-02-10 23:00 | 1770782400 | 1 | 0.5056 | 1.109 | 141.82 | 116.41 | 4.129
2026-02-11 01:00 | 1770789600 | 1 | 0.6139 | 1.309 | 143.61 | 118.14 | 4.887
2026-02-11 03:00 | 1770796800 | 1 | 0.6639 | 1.389 | 142.86 | 119.45 | 4.764
2026-02-11 04:00 | 1770800400 | 1 | 0.7889 | 1.588 | 123.82 | 110.65 | 3.064
2026-02-11 05:00 | 1770804000 | 1 | 0.8278 | 1.752 | 136.71 | 117.5 | 4.929
2026-02-11 06:00 | 1770807600 | 1 | 0.6583 | 1.323 | 139.28 | 120.44 | 3.65
2026-02-11 07:00 | 1770811200 | 1 | 0.7722 | 1.649 | 129.37 | 111.31 | 4.363
2026-02-11 08:00 | 1770814800 | 1 | 0.5306 | 1.065 | 146.84 | 124.14 | 3.543
2026-02-11 09:00 | 1770818400 | 1 | 0.7222 | 1.55 | 119.81 | 104.13 | 3.562
2026-02-11 10:00 | 1770822000 | 1 | 0.6139 | 1.221 | 135.56 | 114.82 | 3.713
2026-02-11 11:00 | 1770825600 | 1 | 0.5639 | 1.176 | 129.41 | 111.31 | 3.121
2026-02-11 12:00 | 1770829200 | 1 | 0.7639 | 1.503 | 122.27 | 105.5 | 3.695
2026-02-11 13:00 | 1770832800 | 0.9528 | 0.7726 | 1.557 | 119.96 | 108.5 | 2.491
2026-02-11 14:00 | 1770836400 | 1 | 0.7056 | 1.384 | 127.12 | 107.77 | 3.923
2026-02-11 15:00 | 1770840000 | 1 | 0.6778 | 1.365 | 123.97 | 110.6 | 2.676
2026-02-11 16:00 | 1770843600 | 1 | 0.4611 | 0.916 | 133.09 | 108.37 | 3.306
2026-02-11 17:00 | 1770847200 | 1 | 0.3111 | 0.579 | 125.92 | 97.91 | 2.375
2026-02-11 18:00 | 1770850800 | 0.9528 | 0.4023 | 0.812 | 123.88 | 107.11 | 1.901
2026-02-11 19:00 | 1770854400 | 1 | 0.4861 | 0.94 | 124.6 | 95.4 | 4.019
2026-02-11 21:00 | 1770861600 | 1 | 0.7694 | 1.642 | 132.57 | 113.51 | 4.585
2026-02-11 22:00 | 1770865200 | 1 | 0.975 | 1.96 | 133.99 | 119 | 4.305
2026-02-11 23:00 | 1770868800 | 1 | 0.6667 | 1.438 | 145.9 | 122.35 | 4.959
2026-02-12 00:00 | 1770872400 | 1 | 0.7444 | 1.504 | 128.46 | 113.54 | 3.286
2026-02-12 01:00 | 1770876000 | 1 | 0.675 | 1.357 | 145.1 | 123.31 | 4.334
2026-02-12 02:00 | 1770879600 | 1 | 0.5583 | 1.212 | 139.62 | 115.24 | 4.328
2026-02-12 03:00 | 1770883200 | 1 | 0.625 | 1.264 | 131.1 | 113.78 | 3.201
2026-02-12 04:00 | 1770886800 | 1 | 0.7222 | 1.544 | 137.19 | 115.92 | 4.813
2026-02-12 05:00 | 1770890400 | 1 | 0.7472 | 1.498 | 132.02 | 115.03 | 3.731
2026-02-12 07:00 | 1770897600 | 1 | 0.5417 | 1.092 | 130.9 | 114.68 | 2.596
2026-02-12 08:00 | 1770901200 | 1 | 0.5694 | 1.138 | 141.45 | 117.91 | 3.926
2026-02-12 09:00 | 1770904800 | 1 | 0.4667 | 1.021 | 139.4 | 111.51 | 4.172
2026-02-12 11:00 | 1770912000 | 1 | 0.35 | 0.682 | 128.44 | 104.34 | 2.41
2026-02-12 12:00 | 1770915600 | 1 | 0.3889 | 0.83 | 132.93 | 105.25 | 3.367
2026-02-12 13:00 | 1770919200 | 1 | 0.4722 | 0.918 | 123.06 | 104.37 | 2.512
2026-02-12 14:00 | 1770922800 | 1 | 0.5 | 0.974 | 119.92 | 103.45 | 2.351
2026-02-12 15:00 | 1770926400 | 1 | 0.4806 | 1.045 | 129.78 | 104.96 | 3.803
2026-02-12 16:00 | 1770930000 | 1 | 0.5167 | 1.008 | 137.39 | 115.75 | 3.196
2026-02-12 17:00 | 1770933600 | 1 | 0.5583 | 1.197 | 138.99 | 114.92 | 4.223
2026-02-12 18:00 | 1770937200 | 1 | 0.4611 | 0.897 | 142.29 | 116.17 | 3.435
2026-02-12 19:00 | 1770940800 | 1 | 0.2861 | 0.619 | 135.18 | 101.79 | 3.029
2026-02-12 20:00 | 1770944400 | 1 | 0.5583 | 1.088 | 137.96 | 114.22 | 3.785
2026-02-12 21:00 | 1770948000 | 1 | 0.55 | 1.172 | 143.6 | 115.75 | 4.781
2026-02-12 22:00 | 1770951600 | 1 | 0.2611 | 0.505 | 135.43 | 109.42 | 1.924
2026-02-12 23:00 | 1770955200 | 1 | 0.5722 | 1.228 | 137.56 | 112.11 | 4.575
2026-02-13 00:00 | 1770958800 | 1 | 0.8444 | 1.784 | 132.15 | 114.1 | 4.718
2026-02-13 01:00 | 1770962400 | 1 | 0.8972 | 1.897 | 149.23 | 127.03 | 6.174
2026-02-13 02:00 | 1770966000 | 1 | 0.8389 | 1.638 | 140.14 | 122.5 | 4.234
2026-02-13 03:00 | 1770969600 | 1 | 0.7972 | 1.67 | 148.36 | 125.48 | 5.597
2026-02-13 04:00 | 1770973200 | 1 | 0.825 | 1.604 | 140.19 | 121.93 | 4.292
2026-02-13 05:00 | 1770976800 | 0.9528 | 0.8192 | 1.7 | 152.57 | 127.45 | 5.964
2026-02-13 06:00 | 1770980400 | 1 | 0.7444 | 1.561 | 141.03 | 120.46 | 4.705
2026-02-13 07:00 | 1770984000 | 1 | 0.8 | 1.589 | 149.12 | 126.71 | 5.218
2026-02-13 08:00 | 1770987600 | 1 | 0.6778 | 1.438 | 149.19 | 121.71 | 5.79
2026-02-13 10:00 | 1770994800 | 1 | 0.4417 | 0.828 | 138.97 | 111.09 | 3.385
2026-02-13 11:00 | 1770998400 | 1 | 0.0889 | 0.171 | 122.63 | 87.6 | 0.88
2026-02-13 12:00 | 1771002000 | 1 | 0.2417 | 0.42 | 122.66 | 86.21 | 2.245
2026-02-13 13:00 | 1771005600 | 1 | 0.0694 | 0.139 | 119.64 | 86.38 | 0.668
2026-02-13 14:00 | 1771009200 | 1 | 0.1306 | 0.215 | 111.19 | 82.92 | 0.882
2026-02-13 15:00 | 1771012800 | 1 | 0.2694 | 0.48 | 142.81 | 91.85 | 3.58
2026-02-13 16:00 | 1771016400 | 1 | 0.2306 | 0.445 | 142.63 | 104.61 | 2.479
2026-02-13 17:00 | 1771020000 | 1 | 0.4167 | 0.917 | 142.96 | 107.96 | 4.693
2026-02-13 18:00 | 1771023600 | 1 | 0.2833 | 0.545 | 145.64 | 113.91 | 2.535
2026-02-13 19:00 | 1771027200 | 1 | 0.3861 | 0.844 | 142.25 | 109.41 | 4.061
2026-02-13 20:00 | 1771030800 | 1 | 0.5083 | 0.988 | 132.74 | 110.08 | 3.282
2026-02-13 21:00 | 1771034400 | 1 | 0.4639 | 1.024 | 149.82 | 117.36 | 4.871
2026-02-13 22:00 | 1771038000 | 1 | 0.65 | 1.556 | 151.23 | 120.02 | 7.117
2026-02-13 23:00 | 1771041600 | 0.9528 | 0.8805 | 1.715 | 137.57 | 118.31 | 4.614
2026-02-14 00:00 | 1771045200 | 1 | 0.6639 | 1.401 | 155.05 | 127.28 | 5.701
2026-02-14 01:00 | 1771048800 | 1 | 0.8056 | 1.564 | 142.58 | 122.75 | 4.544
2026-02-14 02:00 | 1771052400 | 1 | 0.65 | 1.382 | 150.86 | 124.18 | 5.403
2026-02-14 04:00 | 1771059600 | 1 | 0.7722 | 1.521 | 148.09 | 126.81 | 4.742
2026-02-14 05:00 | 1771063200 | 1 | 0.9139 | 1.918 | 136.99 | 119.01 | 5.055
2026-02-14 06:00 | 1771066800 | 1 | 0.9167 | 1.87 | 154.96 | 129.92 | 6.863
2026-02-14 07:00 | 1771070400 | 1 | 0.7722 | 1.492 | 140.45 | 122.36 | 3.956
2026-02-14 08:00 | 1771074000 | 1 | 0.85 | 1.767 | 148.51 | 125.55 | 5.941
2026-02-14 09:00 | 1771077600 | 1 | 0.6667 | 1.299 | 136.58 | 117.97 | 3.54
2026-02-14 10:00 | 1771081200 | 1 | 0.6028 | 1.295 | 121.31 | 105.98 | 2.908
2026-02-14 11:00 | 1771084800 | 1 | 0.2417 | 0.495 | 132.19 | 101.05 | 2.247
2026-02-14 12:00 | 1771088400 | 1 | 0.3667 | 0.773 | 131.32 | 101.94 | 3.327
2026-02-14 13:00 | 1771092000 | 1 | 0.5139 | 1.055 | 113.79 | 98.31 | 2.393
2026-02-14 14:00 | 1771095600 | 1 | 0.6194 | 1.25 | 134.93 | 114.7 | 3.704
2026-02-14 15:00 | 1771099200 | 1 | 0.425 | 0.938 | 128.26 | 103.5 | 3.404
2026-02-14 16:00 | 1771102800 | 1 | 0.4833 | 0.974 | 133.48 | 112.19 | 3.031
2026-02-14 17:00 | 1771106400 | 1 | 0.4167 | 0.833 | 137.09 | 110.59 | 3.237
2026-02-14 18:00 | 1771110000 | 1 | 0.5139 | 1.036 | 132.03 | 107.49 | 3.724
2026-02-14 19:00 | 1771113600 | 1 | 0.5056 | 0.991 | 138.38 | 110.52 | 4.036
2026-02-14 20:00 | 1771117200 | 1 | 0.2556 | 0.51 | 147.04 | 113.81 | 2.483
2026-02-14 21:00 | 1771120800 | 1 | 0.4667 | 0.9 | 143.72 | 107.47 | 4.773
2026-02-14 22:00 | 1771124400 | 1 | 0.5722 | 1.146 | 131.44 | 112.47 | 3.185
2026-02-14 23:00 | 1771128000 | 1 | 0.7861 | 1.539 | 147.15 | 122.03 | 5.665
2026-02-15 00:00 | 1771131600 | 1 | 0.6944 | 1.353 | 138.39 | 116.27 | 4.384
2026-02-15 01:00 | 1771135200 | 1 | 0.7 | 1.398 | 147.65 | 123.27 | 4.992
2026-02-15 02:00 | 1771138800 | 1 | 0.4917 | 0.998 | 156.35 | 123.9 | 4.748
2026-02-15 03:00 | 1771142400 | 1 | 0.6667 | 1.345 | 135.62 | 115.47 | 3.972
2026-02-15 04:00 | 1771146000 | 1 | 0.6528 | 1.406 | 149.23 | 123.72 | 5.256
2026-02-15 05:00 | 1771149600 | 1 | 0.8167 | 1.715 | 136.34 | 116.18 | 5.064
2026-02-15 06:00 | 1771153200 | 1 | 0.8194 | 1.657 | 147.66 | 123.4 | 5.891
2026-02-15 07:00 | 1771156800 | 1 | 0.5611 | 1.125 | 154.57 | 129.76 | 4.092
2026-02-15 08:00 | 1771160400 | 1 | 0.7444 | 1.547 | 134.97 | 115.18 | 4.486
2026-02-15 09:00 | 1771164000 | 1 | 0.85 | 1.809 | 139.1 | 117.85 | 5.635
2026-02-15 10:00 | 1771167600 | 1 | 0.4917 | 0.986 | 140.46 | 117.28 | 3.348
2026-02-15 11:00 | 1771171200 | 1 | 0.1722 | 0.309 | 126.45 | 92.03 | 1.555
2026-02-15 12:00 | 1771174800 | 1 | 0.1944 | 0.39 | 121.85 | 90.37 | 1.797
2026-02-15 13:00 | 1771178400 | 1 | 0.0778 | 0.12 | 120.13 | 79.61 | 0.709
2026-02-15 14:00 | 1771182000 | 1 | 0.1667 | 0.334 | 118.54 | 81.65 | 1.8
2026-02-15 15:00 | 1771185600 | 1 | 0.3056 | 0.693 | 119.67 | 92.52 | 2.757
2026-02-15 16:00 | 1771189200 | 1 | 0.5694 | 1.146 | 135.27 | 112.72 | 3.787
2026-02-15 17:00 | 1771192800 | 1 | 0.6556 | 1.273 | 147.33 | 118.2 | 5.433
2026-02-15 18:00 | 1771196400 | 1 | 0.4722 | 0.948 | 139.04 | 115.74 | 3.236
2026-02-15 19:00 | 1771200000 | 1 | 0.4611 | 0.957 | 142.1 | 113.28 | 4.041
2026-02-15 20:00 | 1771203600 | 1 | 0.4306 | 0.925 | 144.42 | 109.76 | 4.697
2026-02-15 21:00 | 1771207200 | 1 | 0.5528 | 1.107 | 131.01 | 111.83 | 3.11
2026-02-15 22:00 | 1771210800 | 1 | 0.6583 | 1.413 | 148.12 | 120.63 | 5.69
2026-02-15 23:00 | 1771214400 | 1 | 0.6861 | 1.466 | 143.93 | 121.18 | 4.889
2026-02-16 00:00 | 1771218000 | 1 | 0.725 | 1.419 | 154.47 | 124.67 | 6.201
2026-02-16 01:00 | 1771221600 | 1 | 0.5111 | 1.014 | 155.82 | 129.58 | 3.899
2026-02-16 02:00 | 1771225200 | 1 | 0.8 | 1.553 | 143.39 | 119.41 | 5.456
2026-02-16 03:00 | 1771228800 | 1 | 0.5833 | 1.188 | 158.19 | 126.68 | 5.478
2026-02-16 04:00 | 1771232400 | 1 | 0.7167 | 1.523 | 141.13 | 119.69 | 4.783
2026-02-16 05:00 | 1771236000 | 1 | 0.7639 | 1.541 | 148.32 | 126.22 | 4.989
2026-02-16 06:00 | 1771239600 | 1 | 0.7917 | 1.691 | 143.07 | 123.11 | 4.94
2026-02-16 07:00 | 1771243200 | 0.9528 | 0.8397 | 1.709 | 161.79 | 131.64 | 7.197
2026-02-16 08:00 | 1771246800 | 1 | 0.3889 | 0.775 | 160.88 | 129.45 | 3.568
2026-02-16 09:00 | 1771250400 | 1 | 0.5028 | 0.972 | 156.44 | 117.26 | 5.583
2026-02-16 10:00 | 1771254000 | 1 | 0.0944 | 0.188 | 152.67 | 104.01 | 1.334
2026-02-16 11:00 | 1771257600 | 1 | 0.1611 | 0.279 | 146.16 | 88.46 | 2.358
2026-02-16 12:00 | 1771261200 | 1 | 0.0917 | 0.186 | 133.04 | 91.44 | 1.127
2026-02-16 13:00 | 1771264800 | 1 | 0.2056 | 0.407 | 123.24 | 91.58 | 1.887
2026-02-16 14:00 | 1771268400 | 1 | 0.2 | 0.488 | 117.84 | 88.15 | 2.118
2026-02-16 15:00 | 1771272000 | 1 | 0.3222 | 0.65 | 128.34 | 100.7 | 2.631
2026-02-16 16:00 | 1771275600 | 1 | 0.5194 | 1.014 | 130.93 | 109.04 | 3.244
2026-02-16 17:00 | 1771279200 | 1 | 0.6083 | 1.218 | 136.38 | 114.6 | 3.887
2026-02-16 18:00 | 1771282800 | 1 | 0.5389 | 1.067 | 135.38 | 111.74 | 3.703
2026-02-16 19:00 | 1771286400 | 1 | 0.4611 | 0.956 | 128.07 | 105.15 | 3.206
2026-02-16 20:00 | 1771290000 | 1 | 0.6361 | 1.223 | 133.6 | 111.4 | 3.98
2026-02-16 21:00 | 1771293600 | 1 | 0.575 | 1.144 | 137.53 | 116.04 | 3.597
2026-02-16 22:00 | 1771297200 | 1 | 0.6306 | 1.37 | 127.72 | 107.15 | 4.129
2026-02-16 23:00 | 1771300800 | 1 | 0.6694 | 1.292 | 149.29 | 119.17 | 5.701
2026-02-17 00:00 | 1771304400 | 1 | 0.4722 | 0.948 | 142.07 | 116.3 | 3.58
2026-02-17 01:00 | 1771308000 | 1 | 0.7028 | 1.375 | 129.44 | 110.37 | 3.841
2026-02-17 02:00 | 1771311600 | 1 | 0.7111 | 1.538 | 133.43 | 114.21 | 4.327
2026-02-17 03:00 | 1771315200 | 0.95 | 0.7778 | 1.6 | 140.48 | 114.92 | 5.693
2026-02-17 04:00 | 1771318800 | 1 | 0.5778 | 1.26 | 143.2 | 117.43 | 4.755
2026-02-17 05:00 | 1771322400 | 1 | 0.675 | 1.362 | 131.62 | 113.33 | 3.639
2026-02-17 06:00 | 1771326000 | 1 | 0.7611 | 1.486 | 144.78 | 119.85 | 5.426
2026-02-17 07:00 | 1771329600 | 1 | 0.5389 | 1.184 | 146.62 | 116.63 | 5.202
2026-02-17 08:00 | 1771333200 | 1 | 0.4778 | 0.968 | 132.44 | 109.43 | 3.265
2026-02-17 09:00 | 1771336800 | 1 | 0.3889 | 0.829 | 151.76 | 114.19 | 4.559
2026-02-17 10:00 | 1771340400 | 1 | 0.0944 | 0.191 | 147.55 | 99.81 | 1.331
2026-02-17 11:00 | 1771344000 | 1 | 0.0194 | 0.048 | 128.77 | 71.07 | 0.409
2026-02-17 12:00 | 1771347600 | 1 | 0.1778 | 0.388 | 145.66 | 86.31 | 3.361
2026-02-17 13:00 | 1771351200 | 1 | 0.2167 | 0.441 | 144.4 | 102.77 | 2.689
2026-02-17 14:00 | 1771354800 | 1 | 0.4611 | 0.923 | 124.59 | 99.69 | 3.368
2026-02-17 15:00 | 1771358400 | 1 | 0.5361 | 1.076 | 132.35 | 112.06 | 3.199
2026-02-17 16:00 | 1771362000 | 1 | 0.7778 | 1.547 | 123.71 | 106.48 | 3.902
2026-02-17 17:00 | 1771365600 | 1 | 0.4333 | 0.867 | 140.68 | 113.66 | 3.429
2026-02-17 18:00 | 1771369200 | 1 | 0.3778 | 0.861 | 136.01 | 104.31 | 3.993
2026-02-17 19:00 | 1771372800 | 1 | 0.2417 | 0.484 | 134.43 | 105.33 | 2.061
2026-02-17 20:00 | 1771376400 | 1 | 0.3972 | 0.853 | 122.35 | 96.66 | 3.208
2026-02-17 21:00 | 1771380000 | 1 | 0.5056 | 1.101 | 120.34 | 101.51 | 3.037
2026-02-17 22:00 | 1771383600 | 1 | 0.8 | 1.642 | 121.93 | 106.67 | 3.674
2026-02-17 23:00 | 1771387200 | 1 | 0.6111 | 1.298 | 142.64 | 115.91 | 5.08
2026-02-18 00:00 | 1771390800 | 0.9972 | 0.3454 | 0.697 | 131.36 | 108.87 | 2.291
2026-02-18 01:00 | 1771394400 | 1 | 0.5778 | 1.234 | 127.16 | 106.78 | 3.686
2026-02-18 02:00 | 1771398000 | 1 | 0.5056 | 1.113 | 135.13 | 109.51 | 4.176
2026-02-18 03:00 | 1771401600 | 1 | 0.6083 | 1.212 | 131.05 | 107.27 | 4.221
2026-02-18 04:00 | 1771405200 | 1 | 0.45 | 0.91 | 140.74 | 115.35 | 3.382
2026-02-18 05:00 | 1771408800 | 1 | 0.5278 | 1.159 | 131.16 | 109.49 | 3.681
2026-02-18 06:00 | 1771412400 | 1 | 0.5917 | 1.191 | 141.14 | 117.54 | 4.119
2026-02-18 07:00 | 1771416000 | 1 | 0.5889 | 1.141 | 139.92 | 110.67 | 4.886
2026-02-18 08:00 | 1771419600 | 1 | 0.35 | 0.708 | 123.96 | 104.27 | 2.042
2026-02-18 09:00 | 1771423200 | 1 | 0.45 | 1.006 | 128.02 | 102.05 | 3.827
2026-02-18 10:00 | 1771426800 | 1 | 0.2167 | 0.437 | 133.84 | 102.83 | 1.987
2026-02-18 11:00 | 1771430400 | 1 | 0 | 0 |  |  | 0
2026-02-18 12:00 | 1771434000 | 1 | 0.0833 | 0.168 | 131.35 | 77.83 | 1.32
2026-02-18 13:00 | 1771437600 | 1 | 0.0833 | 0.171 | 129.44 | 85.28 | 1.106
2026-02-18 14:00 | 1771441200 | 1 | 0.0944 | 0.191 | 127.17 | 85.83 | 1.158
2026-02-18 15:00 | 1771444800 | 1 | 0.2389 | 0.484 | 126.88 | 91.21 | 2.531
2026-02-18 16:00 | 1771448400 | 1 | 0.4556 | 0.949 | 129.13 | 101.36 | 3.856
2026-02-18 17:00 | 1771452000 | 1 | 0.5222 | 1.129 | 131.26 | 106.47 | 4.1
2026-02-18 18:00 | 1771455600 | 1 | 0.6278 | 1.269 | 125.61 | 108.14 | 3.25
2026-02-18 19:00 | 1771459200 | 1 | 0.775 | 1.56 | 124.71 | 106.99 | 4.043
2026-02-18 20:00 | 1771462800 | 1 | 0.825 | 1.718 | 134.02 | 113.95 | 5.056
2026-02-18 21:00 | 1771466400 | 1 | 0.65 | 1.304 | 143.9 | 121.99 | 4.186
2026-02-18 22:00 | 1771470000 | 1 | 0.5528 | 1.163 | 142.63 | 116.01 | 4.539
2026-02-18 23:00 | 1771473600 | 1 | 0.5 | 1.003 | 145.39 | 122.62 | 3.345
2026-02-19 00:00 | 1771477200 | 1 | 0.6417 | 1.369 | 137.53 | 115.22 | 4.471
2026-02-19 01:00 | 1771480800 | 1 | 0.4917 | 1.058 | 153.57 | 119.98 | 5.209
2026-02-19 02:00 | 1771484400 | 1 | 0.3611 | 0.72 | 147.95 | 119.84 | 2.964
2026-02-19 03:00 | 1771488000 | 1 | 0.5861 | 1.243 | 133.47 | 111.43 | 4.015
2026-02-19 04:00 | 1771491600 | 0.9528 | 0.8163 | 1.66 | 147.39 | 123.31 | 5.58
2026-02-19 05:00 | 1771495200 | 1 | 0.7444 | 1.563 | 140.15 | 119.39 | 4.755
2026-02-19 06:00 | 1771498800 | 1 | 0.5833 | 1.265 | 150.35 | 123.15 | 5.043
2026-02-19 07:00 | 1771502400 | 1 | 0.6167 | 1.233 | 147.75 | 123.04 | 4.465
2026-02-19 08:00 | 1771506000 | 1 | 0.4694 | 0.995 | 158.08 | 121.03 | 5.404
2026-02-19 09:00 | 1771509600 | 1 | 0.2667 | 0.54 | 153.87 | 118.09 | 2.823
2026-02-19 10:00 | 1771513200 | 1 | 0.2 | 0.403 | 153.11 | 113.72 | 2.322
2026-02-19 11:00 | 1771516800 | 1 | 0.0833 | 0.166 | 136.14 | 89.85 | 1.126
2026-02-19 12:00 | 1771520400 | 1 | 0.1889 | 0.378 | 124.95 | 92.45 | 1.802
2026-02-19 13:00 | 1771524000 | 1 | 0.2639 | 0.577 | 121.4 | 93.05 | 2.398
2026-02-19 14:00 | 1771527600 | 1 | 0.2278 | 0.456 | 113.19 | 95.58 | 1.177
2026-02-19 15:00 | 1771531200 | 1 | 0.4333 | 0.872 | 131.8 | 105.91 | 3.304
2026-02-19 16:00 | 1771534800 | 1 | 0.3444 | 0.69 | 132.5 | 111.75 | 2.099
2026-02-19 17:00 | 1771538400 | 1 | 0.1667 | 0.297 | 125.62 | 83.74 | 1.817
2026-02-19 18:00 | 1771542000 | 1 | 0.2583 | 0.475 | 141.07 | 95.26 | 3.187
2026-02-19 19:00 | 1771545600 | 1 | 0.2722 | 0.548 | 139.98 | 108.42 | 2.53
2026-02-19 20:00 | 1771549200 | 1 | 0.3722 | 0.804 | 134.48 | 103.98 | 3.592
2026-02-19 21:00 | 1771552800 | 1 | 0.3528 | 0.736 | 156.01 | 114.15 | 4.514
2026-02-19 22:00 | 1771556400 | 1 | 0.2278 | 0.459 | 153.13 | 113.06 | 2.69
2026-02-19 23:00 | 1771560000 | 1 | 0.3222 | 0.605 | 153.29 | 109.94 | 3.841
2026-02-20 00:00 | 1771563600 | 1 | 0.3611 | 0.756 | 159.43 | 111.81 | 5.275
2026-02-20 01:00 | 1771567200 | 1 | 0.2611 | 0.522 | 164.14 | 119.43 | 3.418
2026-02-20 02:00 | 1771570800 | 1 | 0.3083 | 0.581 | 163.6 | 113.84 | 4.23
2026-02-20 03:00 | 1771574400 | 1 | 0.3889 | 0.887 | 136.88 | 107.71 | 3.79
2026-02-20 04:00 | 1771578000 | 1 | 0.4222 | 0.947 | 155.09 | 120.46 | 4.807
2026-02-20 05:00 | 1771581600 | 1 | 0.4778 | 0.956 | 149.93 | 121.25 | 4.017
2026-02-20 06:00 | 1771585200 | 1 | 0.7167 | 1.506 | 129.08 | 109.89 | 4.235
2026-02-20 07:00 | 1771588800 | 1 | 0.7417 | 1.559 | 149.89 | 122.87 | 6.177
2026-02-20 08:00 | 1771592400 | 1 | 0.4694 | 0.912 | 161.43 | 121.73 | 5.303
2026-02-20 09:00 | 1771596000 | 1 | 0.3278 | 0.66 | 158.3 | 119.9 | 3.716
2026-02-20 10:00 | 1771599600 | 1 | 0.1778 | 0.318 | 156.09 | 103.85 | 2.435
2026-02-20 11:00 | 1771603200 | 1 | 0.0778 | 0.157 | 151.72 | 89.55 | 1.426
2026-02-20 12:00 | 1771606800 | 1 | 0.0833 | 0.167 | 150.09 | 90.55 | 1.456
2026-02-20 13:00 | 1771610400 | 1 | 0.2278 | 0.446 | 150.13 | 93.04 | 3.722
2026-02-20 14:00 | 1771614000 | 1 | 0.1111 | 0.222 | 141.02 | 100.35 | 1.324
2026-02-20 15:00 | 1771617600 | 1 | 0.2556 | 0.515 | 128.87 | 96.5 | 2.429
2026-02-20 16:00 | 1771621200 | 1 | 0.35 | 0.785 | 136.06 | 105.76 | 3.481
2026-02-20 17:00 | 1771624800 | 1 | 0.5 | 0.999 | 134.17 | 110.93 | 3.404
2026-02-20 18:00 | 1771628400 | 1 | 0.4694 | 0.929 | 145.88 | 112.87 | 4.493
2026-02-20 19:00 | 1771632000 | 1 | 0.3583 | 0.693 | 139.75 | 108.65 | 3.156
2026-02-20 20:00 | 1771635600 | 1 | 0.3833 | 0.769 | 133.75 | 107.45 | 2.963
2026-02-20 21:00 | 1771639200 | 1 | 0.6139 | 1.272 | 141.35 | 116.01 | 4.724
2026-02-20 22:00 | 1771642800 | 1 | 0.9472 | 1.908 | 134.65 | 116.63 | 5.04
2026-02-20 23:00 | 1771646400 | 1 | 0.6139 | 1.228 | 154.21 | 129.08 | 4.522
2026-02-21 00:00 | 1771650000 | 1 | 0.5833 | 1.265 | 141.01 | 115.05 | 4.812
2026-02-21 01:00 | 1771653600 | 1 | 0.5 | 1.005 | 152.29 | 124.76 | 4.05
2026-02-21 02:00 | 1771657200 | 1 | 0.5333 | 1.173 | 148.89 | 119.98 | 4.958
2026-02-21 03:00 | 1771660800 | 1 | 0.6944 | 1.496 | 140.3 | 116.38 | 5.242
2026-02-21 04:00 | 1771664400 | 1 | 0.5389 | 1.177 | 156.47 | 125.98 | 5.261
2026-02-21 05:00 | 1771668000 | 1 | 0.65 | 1.305 | 144.33 | 121.45 | 4.372
2026-02-21 06:00 | 1771671600 | 1 | 0.6083 | 1.321 | 149.93 | 122.19 | 5.367
2026-02-21 07:00 | 1771675200 | 1 | 0.8028 | 1.609 | 141.99 | 120.32 | 5.11
2026-02-21 08:00 | 1771678800 | 1 | 0.75 | 1.505 | 145.09 | 123.6 | 4.74
2026-02-21 09:00 | 1771682400 | 1 | 0.4528 | 1.004 | 145.33 | 116.99 | 4.17
2026-02-21 10:00 | 1771686000 | 1 | 0.5278 | 1.015 | 135.09 | 108.74 | 3.914
2026-02-21 11:00 | 1771689600 | 1 | 0 | 0 |  |  | 0
2026-02-21 12:00 | 1771693200 | 1 | 0.1556 | 0.269 | 129.11 | 80.74 | 1.906
2026-02-21 13:00 | 1771696800 | 1 | 0.0833 | 0.171 | 125.07 | 82.94 | 1.047
2026-02-21 14:00 | 1771700400 | 1 | 0.2111 | 0.465 | 121.27 | 85.46 | 2.439
2026-02-21 15:00 | 1771704000 | 1 | 0.2139 | 0.432 | 132.02 | 96.41 | 2.245
2026-02-21 16:00 | 1771707600 | 1 | 0.2333 | 0.542 | 128.6 | 94.25 | 2.727
2026-02-21 17:00 | 1771711200 | 1 | 0.4861 | 0.983 | 123.54 | 102.42 | 3.043
2026-02-21 18:00 | 1771714800 | 1 | 0.4056 | 0.828 | 136.94 | 110.97 | 3.152
2026-02-21 19:00 | 1771718400 | 1 | 0.5139 | 1.082 | 131.21 | 107.01 | 3.843
2026-02-21 20:00 | 1771722000 | 1 | 0.3556 | 0.687 | 144.31 | 115.47 | 2.906
2026-02-21 21:00 | 1771725600 | 1 | 0.3917 | 0.803 | 137.78 | 103.28 | 4.058
2026-02-21 22:00 | 1771729200 | 1 | 0.4667 | 0.878 | 137.64 | 106.77 | 3.972
2026-02-21 23:00 | 1771732800 | 1 | 0.5944 | 1.172 | 141.96 | 120.68 | 3.654
2026-02-22 00:00 | 1771736400 | 1 | 0.9556 | 2.027 | 131.92 | 114.49 | 5.178
2026-02-22 01:00 | 1771740000 | 1 | 0.7722 | 1.636 | 153.74 | 127.46 | 6.298
2026-02-22 02:00 | 1771743600 | 1 | 0.8722 | 1.662 | 138.12 | 118.96 | 4.666
2026-02-22 03:00 | 1771747200 | 1 | 0.8667 | 1.678 | 143.36 | 123.89 | 4.787
2026-02-22 04:00 | 1771750800 | 1 | 1 | 2.104 | 137.5 | 120.16 | 5.347
2026-02-22 05:00 | 1771754400 | 1 | 0.7806 | 1.676 | 148.41 | 125.04 | 5.738
2026-02-22 06:00 | 1771758000 | 1 | 1 | 2.085 | 132.53 | 116.54 | 4.887
2026-02-22 07:00 | 1771761600 | 1 | 0.8917 | 1.876 | 152.39 | 128.36 | 6.605
2026-02-22 08:00 | 1771765200 | 1 | 0.7889 | 1.534 | 130.44 | 116.18 | 3.206
2026-02-22 09:00 | 1771768800 | 1 | 0.7722 | 1.613 | 142.86 | 119.33 | 5.558
2026-02-22 10:00 | 1771772400 | 1 | 0.2722 | 0.527 | 143.98 | 118.67 | 1.953
2026-02-22 11:00 | 1771776000 | 1 | 0.1667 | 0.283 | 127.29 | 82.5 | 1.845
2026-02-22 12:00 | 1771779600 | 1 | 0.0833 | 0.163 | 122.56 | 83.03 | 0.942
2026-02-22 13:00 | 1771783200 | 1 | 0.0833 | 0.16 | 120.53 | 79.84 | 0.952
2026-02-22 14:00 | 1771786800 | 1 | 0.0889 | 0.173 | 120.03 | 83.54 | 0.923
2026-02-22 15:00 | 1771790400 | 1 | 0.2083 | 0.403 | 119.51 | 88.75 | 1.817
2026-02-22 16:00 | 1771794000 | 1 | 0.4583 | 0.931 | 120.85 | 99.34 | 2.936
2026-02-22 17:00 | 1771797600 | 1 | 0.5306 | 1.155 | 132.15 | 107.86 | 4.108
2026-02-22 18:00 | 1771801200 | 1 | 0.7333 | 1.428 | 127.35 | 110.08 | 3.615
2026-02-22 19:00 | 1771804800 | 1 | 0.3833 | 0.856 | 146.12 | 114.53 | 3.964
2026-02-22 20:00 | 1771808400 | 1 | 0.5194 | 0.967 | 141.37 | 109.51 | 4.513
2026-02-22 21:00 | 1771812000 | 1 | 0.3556 | 0.696 | 150.61 | 114.6 | 3.668
2026-02-22 22:00 | 1771815600 | 1 | 0.4472 | 0.829 | 138.77 | 111.12 | 3.356
2026-02-22 23:00 | 1771819200 | 1 | 0.525 | 1.059 | 151.1 | 117.76 | 5.175
2026-02-23 00:00 | 1771822800 | 1 | 0.5417 | 1.05 | 142.06 | 117.88 | 3.72
2026-02-23 01:00 | 1771826400 | 1 | 0.4972 | 1.053 | 144.2 | 114.61 | 4.561
2026-02-23 02:00 | 1771830000 | 1 | 0.4944 | 0.947 | 139.64 | 117.98 | 3.006
2026-02-23 03:00 | 1771833600 | 1 | 0.7583 | 1.604 | 132.68 | 112.13 | 4.829
2026-02-23 04:00 | 1771837200 | 1 | 0.5972 | 1.156 | 150.15 | 122.82 | 4.626
2026-02-23 05:00 | 1771840800 | 1 | 0.625 | 1.304 | 136.82 | 113.53 | 4.452
2026-02-23 06:00 | 1771844400 | 1 | 0.6194 | 1.152 | 147.57 | 117.89 | 5.004
2026-02-23 07:00 | 1771848000 | 1 | 0.4167 | 0.814 | 143.31 | 116.04 | 3.246
2026-02-23 08:00 | 1771851600 | 1 | 0.4417 | 0.938 | 149.5 | 117.88 | 4.346
2026-02-23 09:00 | 1771855200 | 1 | 0.4806 | 0.898 | 156.18 | 116.71 | 5.196
2026-02-23 10:00 | 1771858800 | 1 | 0.2833 | 0.629 | 155.2 | 113.61 | 3.833
2026-02-23 11:00 | 1771862400 | 1 | 0.4056 | 0.787 | 148.99 | 116.42 | 3.755
2026-02-23 12:00 | 1771866000 | 1 | 0.6222 | 1.334 | 123.53 | 106.06 | 3.415
2026-02-23 13:00 | 1771869600 | 1 | 0.875 | 1.85 | 127.14 | 111.47 | 4.248
2026-02-23 14:00 | 1771873200 | 1 | 0.8389 | 1.634 | 141.06 | 118.14 | 5.475
2026-02-23 15:00 | 1771876800 | 1 | 0.8083 | 1.523 | 135.98 | 116.96 | 4.245
2026-02-23 16:00 | 1771880400 | 1 | 1 | 2.087 | 139.46 | 120.84 | 5.695
2026-02-23 17:00 | 1771884000 | 1 | 0.7917 | 1.59 | 139.65 | 119.05 | 4.8
2026-02-23 18:00 | 1771887600 | 1 | 0.4556 | 0.888 | 129.87 | 110.31 | 2.544
2026-02-23 19:00 | 1771891200 | 1 | 0.4639 | 1.004 | 121.6 | 101.8 | 2.912
2026-02-23 20:00 | 1771894800 | 1 | 0.4306 | 0.764 | 133.05 | 99.73 | 3.728
2026-02-23 21:00 | 1771898400 | 1 | 0.5111 | 0.971 | 142.41 | 114.86 | 3.92
2026-02-23 22:00 | 1771902000 | 1 | 0.4972 | 1.094 | 137.83 | 111.75 | 4.179
2026-02-23 23:00 | 1771905600 | 1 | 0.7333 | 1.561 | 134.56 | 115.24 | 4.418
2026-02-24 00:00 | 1771909200 | 1 | 0.8472 | 1.626 | 140.26 | 118.56 | 5.17
2026-02-24 01:00 | 1771912800 | 1 | 0.6111 | 1.19 | 144.67 | 124.3 | 3.55
2026-02-24 02:00 | 1771916400 | 1 | 0.7111 | 1.471 | 139.5 | 115.45 | 5.183
2026-02-24 03:00 | 1771920000 | 1 | 0.5972 | 1.283 | 140.71 | 118.24 | 4.223
2026-02-24 04:00 | 1771923600 | 1 | 0.7139 | 1.496 | 132.71 | 112.2 | 4.495
2026-02-24 05:00 | 1771927200 | 1 | 0.6778 | 1.312 | 149.33 | 126.02 | 4.481
2026-02-24 06:00 | 1771930800 | 1 | 0.6639 | 1.245 | 134.95 | 114.17 | 3.792
2026-02-24 07:00 | 1771934400 | 1 | 0.5028 | 1.091 | 156.62 | 120.53 | 5.759
2026-02-24 08:00 | 1771938000 | 1 | 0.3583 | 0.697 | 152.43 | 116.02 | 3.716
2026-02-24 09:00 | 1771941600 | 1 | 0.35 | 0.632 | 151.96 | 110.44 | 3.844
2026-02-24 10:00 | 1771945200 | 1 | 0.2361 | 0.517 | 149.6 | 102.19 | 3.595
2026-02-24 11:00 | 1771948800 | 1 | 0.2444 | 0.477 | 132.3 | 104.51 | 1.941
2026-02-24 12:00 | 1771952400 | 1 | 0.4833 | 1.023 | 128.92 | 102.43 | 3.972
2026-02-24 13:00 | 1771956000 | 1 | 0.425 | 0.824 | 132.18 | 108.7 | 2.836
2026-02-24 14:00 | 1771959600 | 1 | 0.3778 | 0.737 | 119.86 | 100.28 | 2.112
2026-02-24 15:00 | 1771963200 | 1 | 0.4056 | 0.832 | 140.61 | 109.71 | 3.771
2026-02-24 16:00 | 1771966800 | 1 | 0.5333 | 1.037 | 135.63 | 113.03 | 3.433
2026-02-24 17:00 | 1771970400 | 1 | 0.5722 | 1.123 | 149.83 | 117.7 | 5.287
2026-02-24 18:00 | 1771974000 | 1 | 0.3139 | 0.609 | 136.96 | 107.49 | 2.624
2026-02-24 19:00 | 1771977600 | 1 | 0.4 | 0.753 | 139.21 | 107.48 | 3.5
2026-02-24 20:00 | 1771981200 | 1 | 0.7528 | 1.46 | 131.57 | 109.01 | 4.828
2026-02-24 21:00 | 1771984800 | 1 | 0.8194 | 1.539 | 155.01 | 126.63 | 6.401
2026-02-24 22:00 | 1771988400 | 1 | 0.7667 | 1.488 | 151.75 | 127.94 | 5.193
2026-02-24 23:00 | 1771992000 | 1 | 0.7722 | 1.588 | 149.51 | 124.91 | 5.722
2026-02-25 00:00 | 1771995600 | 0.9972 | 0.7326 | 1.546 | 158.64 | 129.35 | 6.614
2026-02-25 01:00 | 1771999200 | 1 | 0.5778 | 1.116 | 152.09 | 126.55 | 4.176
2026-02-25 02:00 | 1772002800 | 1 | 0.575 | 1.234 | 158.26 | 126.45 | 5.744
2026-02-25 03:00 | 1772006400 | 1 | 0.8028 | 1.706 | 140.15 | 119.1 | 5.263
2026-02-25 04:00 | 1772010000 | 1 | 0.7778 | 1.457 | 158.33 | 130.29 | 5.986
2026-02-25 05:00 | 1772013600 | 1 | 0.6583 | 1.372 | 144.6 | 122.36 | 4.473
2026-02-25 06:00 | 1772017200 | 1 | 0.8944 | 1.924 | 147.46 | 124.39 | 6.508
2026-02-25 07:00 | 1772020800 | 1 | 0.8944 | 1.774 | 154 | 131.29 | 5.903
2026-02-25 08:00 | 1772024400 | 1 | 0.5556 | 1.205 | 167.79 | 131.04 | 6.487
2026-02-25 09:00 | 1772028000 | 1 | 0.4889 | 1.019 | 166.52 | 128.44 | 5.684
2026-02-25 10:00 | 1772031600 | 1 | 0.4833 | 0.933 | 164.43 | 128.3 | 4.942
2026-02-25 11:00 | 1772035200 | 1 | 0.5056 | 1.087 | 148.79 | 118.95 | 4.754
2026-02-25 12:00 | 1772038800 | 1 | 0.8667 | 1.688 | 126.51 | 112.38 | 3.496
2026-02-25 13:00 | 1772042400 | 1 | 0.775 | 1.608 | 140.32 | 119.34 | 4.941
2026-02-25 14:00 | 1772046000 | 1 | 0.6361 | 1.233 | 127.49 | 109.56 | 3.239
2026-02-25 15:00 | 1772049600 | 1 | 0.7611 | 1.482 | 128.06 | 111.63 | 3.569
2026-02-25 16:00 | 1772053200 | 1 | 0.7056 | 1.486 | 137.84 | 115.88 | 4.781
2026-02-25 17:00 | 1772056800 | 1 | 0.6278 | 1.213 | 148.24 | 118.44 | 5.295
2026-02-25 18:00 | 1772060400 | 0.9528 | 0.3761 | 0.731 | 135.3 | 114.51 | 2.121
2026-02-25 19:00 | 1772064000 | 1 | 0.4306 | 0.91 | 129.34 | 101.97 | 3.649
2026-02-25 20:00 | 1772067600 | 1 | 0.4111 | 0.799 | 134.38 | 107.28 | 3.173
2026-02-25 21:00 | 1772071200 | 1 | 0.3139 | 0.583 | 143.06 | 104.57 | 3.226
2026-02-25 22:00 | 1772074800 | 1 | 0.5194 | 0.992 | 130.11 | 106.71 | 3.398
2026-02-25 23:00 | 1772078400 | 1 | 0.8833 | 1.726 | 127.21 | 112.31 | 3.767
2026-02-26 00:00 | 1772082000 | 1 | 0.8944 | 1.898 | 138.4 | 119.29 | 5.318
2026-02-26 01:00 | 1772085600 | 1 | 0.8 | 1.543 | 147.58 | 124.25 | 5.283
2026-02-26 02:00 | 1772089200 | 1 | 0.7806 | 1.644 | 127.9 | 112.38 | 3.734
2026-02-26 03:00 | 1772092800 | 1 | 0.7861 | 1.524 | 147.78 | 125.19 | 5.045
2026-02-26 04:00 | 1772096400 | 1 | 0.6528 | 1.379 | 144.3 | 119.58 | 4.994
2026-02-26 05:00 | 1772100000 | 1 | 0.7889 | 1.598 | 131.61 | 113.42 | 4.26
2026-02-26 06:00 | 1772103600 | 1 | 0.8917 | 1.872 | 128.15 | 113.66 | 3.975
2026-02-26 07:00 | 1772107200 | 1 | 0.6861 | 1.344 | 151.44 | 126.47 | 4.913
2026-02-26 08:00 | 1772110800 | 1 | 0.5278 | 1.15 | 129.98 | 110.38 | 3.302
2026-02-26 09:00 | 1772114400 | 1 | 0.5806 | 1.171 | 124.59 | 106.26 | 3.146
2026-02-26 10:00 | 1772118000 | 1 | 0.275 | 0.538 | 138.89 | 111.42 | 2.163
2026-02-26 11:00 | 1772121600 | 1 | 0.0833 | 0.168 | 130.27 | 82.96 | 1.167
2026-02-26 12:00 | 1772125200 | 1 | 0.1028 | 0.28 | 129.69 | 84.32 | 1.864
2026-02-26 13:00 | 1772128800 | 1 | 0.0889 | 0.18 | 122.34 | 85.14 | 0.98
2026-02-26 14:00 | 1772132400 | 1 | 0.0944 | 0.191 | 119.81 | 85.12 | 0.97
2026-02-26 15:00 | 1772136000 | 1 | 0.2778 | 0.515 | 120.38 | 89.43 | 2.336
2026-02-26 16:00 | 1772139600 | 1 | 0.2417 | 0.485 | 128.34 | 101.11 | 1.934
2026-02-26 17:00 | 1772143200 | 1 | 0.3167 | 0.591 | 142.49 | 103.13 | 3.41
2026-02-26 18:00 | 1772146800 | 1 | 0.3889 | 0.783 | 137.54 | 109.65 | 3.193
2026-02-26 19:00 | 1772150400 | 1 | 0.4611 | 1.011 | 137.17 | 108.78 | 4.197
2026-02-26 20:00 | 1772154000 | 1 | 0.45 | 0.91 | 136.92 | 112.02 | 3.312
2026-02-26 21:00 | 1772157600 | 1 | 0.3667 | 0.831 | 151.58 | 116.7 | 4.248
2026-02-26 22:00 | 1772161200 | 1 | 0.5194 | 1.024 | 143.57 | 115.05 | 4.279
2026-02-26 23:00 | 1772164800 | 1 | 0.5 | 0.98 | 155.56 | 122.33 | 4.77
2026-02-27 00:00 | 1772168400 | 1 | 0.4583 | 1.03 | 139.71 | 111.86 | 4.202
2026-02-27 01:00 | 1772172000 | 1 | 0.4694 | 0.897 | 160.23 | 123.64 | 4.81
2026-02-27 02:00 | 1772175600 | 1 | 0.4139 | 0.826 | 151.88 | 122.13 | 3.598
2026-02-27 03:00 | 1772179200 | 1 | 0.7028 | 1.456 | 144.79 | 118.32 | 5.646
2026-02-27 04:00 | 1772182800 | 1 | 0.5472 | 1.102 | 154.01 | 122.18 | 5.132
2026-02-27 05:00 | 1772186400 | 1 | 0.675 | 1.352 | 137.43 | 118.91 | 3.669
2026-02-27 06:00 | 1772190000 | 1 | 0.6333 | 1.378 | 152.02 | 124.8 | 5.497
2026-02-27 07:00 | 1772193600 | 1 | 0.7167 | 1.395 | 150.64 | 122.29 | 5.793
2026-02-27 08:00 | 1772197200 | 1 | 0.4028 | 0.806 | 166.87 | 127.21 | 4.674
2026-02-27 09:00 | 1772200800 | 1 | 0.2556 | 0.601 | 164.03 | 114.55 | 4.359
2026-02-27 10:00 | 1772204400 | 1 | 0.2111 | 0.421 | 160.68 | 113.21 | 2.932
2026-02-27 11:00 | 1772208000 | 1 | 0 | 0 |  |  | 0
2026-02-27 12:00 | 1772211600 | 1 | 0.2028 | 0.509 | 139.72 | 91.55 | 3.595
2026-02-27 13:00 | 1772215200 | 1 | 0.2167 | 0.436 | 121.53 | 95.57 | 1.652
2026-02-27 14:00 | 1772218800 | 1 | 0.4444 | 0.893 | 123.1 | 101.2 | 2.866
2026-02-27 15:00 | 1772222400 | 1 | 0.2611 | 0.525 | 135.02 | 108.4 | 2.047
2026-02-27 16:00 | 1772226000 | 1 | 0.3944 | 0.87 | 129.83 | 102.15 | 3.527
2026-02-27 17:00 | 1772229600 | 1 | 0.35 | 0.707 | 144.81 | 114.86 | 3.098
2026-02-27 18:00 | 1772233200 | 1 | 0.2278 | 0.459 | 150.02 | 112.03 | 2.554
2026-02-27 19:00 | 1772236800 | 1 | 0.3083 | 0.618 | 148.53 | 109.27 | 3.555
2026-02-27 20:00 | 1772240400 | 1 | 0.325 | 0.623 | 148.57 | 106.29 | 3.854
2026-02-27 21:00 | 1772244000 | 1 | 0.2278 | 0.457 | 139.64 | 106.99 | 2.185
2026-02-27 22:00 | 1772247600 | 1 | 0.55 | 1.213 | 133.31 | 108.7 | 4.374
2026-02-27 23:00 | 1772251200 | 1 | 0.6944 | 1.428 | 144.88 | 120.75 | 5.05
2026-02-28 00:00 | 1772254800 | 1 | 0.9333 | 1.87 | 136.85 | 120.28 | 4.54
2026-02-28 01:00 | 1772258400 | 1 | 0.7889 | 1.676 | 145.97 | 123.58 | 5.496
2026-02-28 02:00 | 1772262000 | 1 | 0.8917 | 1.865 | 134.78 | 117.36 | 4.764
2026-02-28 03:00 | 1772265600 | 1 | 1 | 2.03 | 135.99 | 120.59 | 4.581
2026-02-28 04:00 | 1772269200 | 1 | 0.8333 | 1.764 | 150.5 | 127.47 | 5.948
2026-02-28 05:00 | 1772272800 | 1 | 0.8111 | 1.627 | 137.91 | 120.27 | 4.207
2026-02-28 06:00 | 1772276400 | 1 | 0.7611 | 1.623 | 134.36 | 115.94 | 4.382
2026-02-28 07:00 | 1772280000 | 1 | 0.8972 | 1.803 | 122.41 | 111.54 | 2.873
2026-02-28 08:00 | 1772283600 | 1 | 1 | 2.109 | 123.28 | 109.99 | 4.11
2026-02-28 09:00 | 1772287200 | 1 | 1 | 2.102 | 125.38 | 111.75 | 4.197
2026-02-28 10:00 | 1772290800 | 1 | 1 | 2.013 | 111.39 | 102.98 | 2.48
2026-02-28 11:00 | 1772294400 | 1 | 1 | 2.016 | 108.51 | 98.79 | 2.872
2026-02-28 12:00 | 1772298000 | 1 | 0.7472 | 1.507 | 114.46 | 105.27 | 2.025
2026-02-28 13:00 | 1772301600 | 1 | 0.3 | 0.606 | 106.67 | 93.11 | 1.203
2026-02-28 14:00 | 1772305200 | 1 | 0.3222 | 0.657 | 113.91 | 93.27 | 1.978
2026-02-28 15:00 | 1772308800 | 1 | 0.3861 | 0.765 | 125.48 | 101.62 | 2.674
2026-02-28 16:00 | 1772312400 | 1 | 0.2167 | 0.433 | 122.73 | 98.98 | 1.508
2026-02-28 17:00 | 1772316000 | 1 | 0.4056 | 0.917 | 116.93 | 93.41 | 3.136
2026-02-28 18:00 | 1772319600 | 1 | 0.2556 | 0.517 | 131.39 | 106.65 | 1.871
2026-02-28 19:00 | 1772323200 | 1 | 0.1889 | 0.384 | 126.1 | 94.72 | 1.767
2026-02-28 20:00 | 1772326800 | 1 | 0.2694 | 0.506 | 125.02 | 91.49 | 2.483
2026-02-28 21:00 | 1772330400 | 1 | 0.2167 | 0.435 | 121.86 | 94.92 | 1.718
2026-02-28 22:00 | 1772334000 | 1 | 0.5833 | 1.27 | 128.43 | 105.67 | 4.231
2026-02-28 23:00 | 1772337600 | 1 | 0.6722 | 1.351 | 125.1 | 110.49 | 2.893
2026-03-01 00:00 | 1772341200 | 1 | 0.7444 | 1.493 | 138.24 | 118.49 | 4.321
2026-03-01 01:00 | 1772344800 | 1 | 0.5444 | 1.188 | 137.34 | 115.43 | 3.814
2026-03-01 02:00 | 1772348400 | 1 | 0.7167 | 1.436 | 134.1 | 114.4 | 4.144
2026-03-01 03:00 | 1772352000 | 1 | 0.45 | 0.979 | 142.53 | 113.54 | 4.159
2026-03-01 04:00 | 1772355600 | 1 | 0.5 | 1.007 | 135.7 | 114.19 | 3.171
2026-03-01 05:00 | 1772359200 | 1 | 0.4222 | 0.935 | 149.39 | 117.79 | 4.332
2026-03-01 06:00 | 1772362800 | 1 | 0.4722 | 0.946 | 142.76 | 117.59 | 3.491
2026-03-01 07:00 | 1772366400 | 1 | 0.6556 | 1.354 | 133.69 | 112.96 | 4.111
2026-03-01 08:00 | 1772370000 | 1 | 0.5889 | 1.282 | 139.15 | 116.69 | 4.219
2026-03-01 09:00 | 1772373600 | 1 | 0.7889 | 1.587 | 129.63 | 113.87 | 3.665
2026-03-01 10:00 | 1772377200 | 1 | 0.65 | 1.306 | 143.66 | 119.2 | 4.678
2026-03-01 11:00 | 1772380800 | 1 | 0.1583 | 0.301 | 137.73 | 110.18 | 1.214
2026-03-01 12:00 | 1772384400 | 1 | 0.0833 | 0.166 | 123.31 | 83.82 | 0.963
2026-03-01 13:00 | 1772388000 | 1 | 0.2444 | 0.478 | 138.88 | 90 | 3.413
2026-03-01 14:00 | 1772391600 | 1 | 0.1056 | 0.212 | 135.32 | 95.96 | 1.222
2026-03-01 15:00 | 1772395200 | 1 | 0.4583 | 0.934 | 129.76 | 103.03 | 3.66
2026-03-01 16:00 | 1772398800 | 1 | 0.6444 | 1.292 | 134.84 | 114.81 | 3.792
2026-03-01 17:00 | 1772402400 | 1 | 0.5222 | 1.027 | 156.34 | 121.42 | 5.253
2026-03-01 18:00 | 1772406000 | 1 | 0.4528 | 0.908 | 150.6 | 119.98 | 4.074
2026-03-01 19:00 | 1772409600 | 1 | 0.6694 | 1.361 | 137.19 | 111.65 | 5.093
2026-03-01 20:00 | 1772413200 | 1 | 0.6444 | 1.344 | 154.65 | 126.94 | 5.452
2026-03-01 21:00 | 1772416800 | 1 | 0.5889 | 1.16 | 164.05 | 126.55 | 6.376
2026-03-01 22:00 | 1772420400 | 1 | 0.5278 | 1.122 | 150 | 122.55 | 4.514
2026-03-01 23:00 | 1772424000 | 1 | 0.8944 | 1.819 | 159.33 | 134.06 | 6.734
2026-03-02 00:00 | 1772427600 | 1 | 0.8833 | 1.855 | 155.85 | 132.07 | 6.463
2026-03-02 01:00 | 1772431200 | 1 | 0.9 | 1.899 | 161.29 | 133.66 | 7.69
2026-03-02 02:00 | 1772434800 | 1 | 0.7694 | 1.535 | 157.49 | 135.05 | 5.048
2026-03-02 03:00 | 1772438400 | 1 | 0.8028 | 1.638 | 163.31 | 134.9 | 6.816
2026-03-02 04:00 | 1772442000 | 1 | 0.85 | 1.653 | 159.51 | 132.69 | 6.496
2026-03-02 05:00 | 1772445600 | 1 | 0.8944 | 1.782 | 162.73 | 137.38 | 6.621
2026-03-02 06:00 | 1772449200 | 1 | 0.6694 | 1.433 | 166.6 | 135.08 | 6.618
2026-03-02 07:00 | 1772452800 | 1 | 0.7694 | 1.558 | 170.56 | 135.44 | 8.02
2026-03-02 08:00 | 1772456400 | 1 | 0.75 | 1.488 | 167.74 | 139.58 | 6.139
2026-03-02 09:00 | 1772460000 | 1 | 0.7944 | 1.629 | 161.78 | 132.56 | 6.971
2026-03-02 10:00 | 1772463600 | 1 | 0.3833 | 0.768 | 161.59 | 130.74 | 3.474
2026-03-02 11:00 | 1772467200 | 1 | 0.4583 | 0.874 | 138.51 | 107.85 | 3.927
2026-03-02 12:00 | 1772470800 | 1 | 0.4861 | 0.953 | 137.38 | 111.4 | 3.626
2026-03-02 13:00 | 1772474400 | 1 | 0.3278 | 0.75 | 136.46 | 107.97 | 3.129
2026-03-02 14:00 | 1772478000 | 1 | 0.4222 | 0.845 | 140.44 | 113.37 | 3.353
2026-03-02 15:00 | 1772481600 | 1 | 0.575 | 1.209 | 139.2 | 112.39 | 4.751
2026-03-02 16:00 | 1772485200 | 1 | 0.5444 | 1.162 | 158.64 | 123.93 | 5.91
2026-03-02 17:00 | 1772488800 | 1 | 0.8722 | 1.754 | 156.12 | 134.39 | 5.586
2026-03-02 18:00 | 1772492400 | 1 | 1 | 2.099 | 141.78 | 123.09 | 5.748
2026-03-02 19:00 | 1772496000 | 1 | 0.9 | 1.804 | 128.77 | 115.63 | 3.473
2026-03-02 20:00 | 1772499600 | 1 | 1 | 2.111 | 131.83 | 116.27 | 4.814
2026-03-02 21:00 | 1772503200 | 1 | 1 | 2.103 | 157.04 | 132.08 | 7.694
2026-03-02 22:00 | 1772506800 | 1 | 0.9028 | 1.895 | 157.82 | 134.55 | 6.461
2026-03-02 23:00 | 1772510400 | 1 | 0.8167 | 1.616 | 161.18 | 134.41 | 6.34
2026-03-03 00:00 | 1772514000 | 1 | 0.6944 | 1.371 | 161.25 | 131.18 | 6.036
2026-03-03 01:00 | 1772517600 | 1 | 0.7611 | 1.632 | 154.11 | 127.65 | 6.315
2026-03-03 02:00 | 1772521200 | 1 | 0.7472 | 1.599 | 157.89 | 131.36 | 6.218
2026-03-03 03:00 | 1772524800 | 0.9528 | 0.8805 | 1.765 | 153.21 | 130.8 | 5.523
2026-03-03 04:00 | 1772528400 | 1 | 1 | 2.11 | 145.58 | 125.83 | 6.106
2026-03-03 05:00 | 1772532000 | 1 | 0.8944 | 1.894 | 159.21 | 133.79 | 7.051
2026-03-03 06:00 | 1772535600 | 1 | 0.9417 | 1.906 | 149.03 | 128.1 | 5.844
2026-03-03 07:00 | 1772539200 | 1 | 0.7833 | 1.555 | 164.83 | 138.54 | 5.992
2026-03-03 08:00 | 1772542800 | 1 | 0.4222 | 0.81 | 147.51 | 111.63 | 4.257
2026-03-03 09:00 | 1772546400 | 1 | 0.575 | 1.249 | 138.59 | 113.38 | 4.612
2026-03-03 10:00 | 1772550000 | 1 | 0.2556 | 0.515 | 156.77 | 119.74 | 2.78
2026-03-03 11:00 | 1772553600 | 1 | 0.2639 | 0.485 | 150.26 | 98.68 | 3.659
2026-03-03 12:00 | 1772557200 | 1 | 0.0889 | 0.179 | 140.28 | 97.25 | 1.131
2026-03-03 13:00 | 1772560800 | 1 | 0.1944 | 0.388 | 154.4 | 105.16 | 2.797
2026-03-03 14:00 | 1772564400 | 1 | 0.1972 | 0.491 | 160.21 | 102.25 | 4.164
2026-03-03 15:00 | 1772568000 | 1 | 0.1528 | 0.309 | 158.02 | 104.39 | 2.412
2026-03-03 16:00 | 1772571600 | 1 | 0.1306 | 0.261 | 157.75 | 105.24 | 2.009
2026-03-03 17:00 | 1772575200 | 1 | 0.2083 | 0.439 | 155.46 | 102.29 | 3.415
2026-03-03 18:00 | 1772578800 | 1 | 0.2056 | 0.41 | 144.98 | 106.28 | 2.323
2026-03-03 19:00 | 1772582400 | 1 | 0.2833 | 0.534 | 141.43 | 102 | 3.087
2026-03-03 20:00 | 1772586000 | 1 | 0.3417 | 0.686 | 132.39 | 106.03 | 2.648
2026-03-03 21:00 | 1772589600 | 1 | 0.2056 | 0.377 | 143.35 | 102.31 | 2.267
2026-03-03 22:00 | 1772593200 | 1 | 0.2056 | 0.412 | 140.18 | 99.23 | 2.473
2026-03-03 23:00 | 1772596800 | 1 | 0.5806 | 1.126 | 132.59 | 107.8 | 4.091
2026-03-04 00:00 | 1772600400 | 0.9972 | 0.6184 | 1.24 | 133.31 | 115.12 | 3.298
2026-03-04 01:00 | 1772604000 | 1 | 0.7611 | 1.624 | 132.04 | 114.1 | 4.27
2026-03-04 02:00 | 1772607600 | 1 | 0.6139 | 1.233 | 140.67 | 120.53 | 3.636
2026-03-04 03:00 | 1772611200 | 1 | 0.6778 | 1.364 | 135.89 | 114.46 | 4.281
2026-03-04 04:00 | 1772614800 | 1 | 0.4806 | 0.964 | 145.53 | 120.6 | 3.52
2026-03-04 05:00 | 1772618400 | 1 | 0.4056 | 0.838 | 146.87 | 116.36 | 3.738
2026-03-04 06:00 | 1772622000 | 1 | 0.4194 | 0.84 | 143.92 | 116.37 | 3.389
2026-03-04 08:00 | 1772629200 | 1 | 0.3806 | 0.768 | 137.13 | 111.08 | 2.925
2026-03-04 09:00 | 1772632800 | 1 | 0.3417 | 0.685 | 136.62 | 113.06 | 2.367
2026-03-04 10:00 | 1772636400 | 1 | 0.1806 | 0.333 | 124.88 | 97.15 | 1.337
2026-03-04 11:00 | 1772640000 | 1 | 0.0778 | 0.156 | 125.62 | 81.68 | 1.006
2026-03-04 12:00 | 1772643600 | 1 | 0 | 0 |  |  | 0
2026-03-04 13:00 | 1772647200 | 1 | 0 | 0 |  |  | 0
2026-03-04 14:00 | 1772650800 | 1 | 0 | 0 |  |  | 0
2026-03-04 15:00 | 1772654400 | 1 | 0.1889 | 0.378 | 136.67 | 87.96 | 2.7
2026-03-04 16:00 | 1772658000 | 1 | 0.1417 | 0.257 | 148.49 | 92.33 | 2.115
2026-03-04 17:00 | 1772661600 | 1 | 0.0944 | 0.191 | 147.22 | 98.58 | 1.359
2026-03-04 18:00 | 1772665200 | 1 | 0 | 0 |  |  | 0
2026-03-04 19:00 | 1772668800 | 1 | 0.1111 | 0.27 | 140.89 | 80.99 | 2.372
2026-03-04 20:00 | 1772672400 | 1 | 0.0833 | 0.167 | 138.62 | 86.71 | 1.271
2026-03-04 21:00 | 1772676000 | 1 | 0.0889 | 0.175 | 139.58 | 93.51 | 1.18
2026-03-04 22:00 | 1772679600 | 1 | 0.3667 | 0.838 | 124.28 | 98.1 | 3.216
2026-03-04 23:00 | 1772683200 | 1 | 0.2917 | 0.619 | 142.76 | 105.72 | 3.342
2026-03-05 00:00 | 1772686800 | 1 | 0.3083 | 0.628 | 135.77 | 106.92 | 2.637
2026-03-05 01:00 | 1772690400 | 1 | 0.4139 | 0.799 | 133.99 | 107 | 3.159
2026-03-05 02:00 | 1772694000 | 1 | 0.4417 | 0.981 | 131.24 | 105.9 | 3.64
2026-03-05 03:00 | 1772697600 | 1 | 0.4778 | 0.961 | 140.26 | 113.43 | 3.777
2026-03-05 04:00 | 1772701200 | 1 | 0.2333 | 0.563 | 157.31 | 112.72 | 3.676
2026-03-05 05:00 | 1772704800 | 1 | 0.2833 | 0.535 | 157.58 | 111.23 | 3.633
2026-03-05 06:00 | 1772708400 | 1 | 0.2722 | 0.544 | 155.34 | 112.92 | 3.384
2026-03-05 07:00 | 1772712000 | 1 | 0.3361 | 0.643 | 157.46 | 108.53 | 4.587
2026-03-05 08:00 | 1772715600 | 1 | 0.2806 | 0.565 | 148.59 | 113.16 | 2.932
2026-03-05 09:00 | 1772719200 | 1 | 0.3722 | 0.714 | 142.56 | 109 | 3.499
2026-03-05 10:00 | 1772722800 | 1 | 0.4694 | 0.946 | 138.72 | 114.57 | 3.342
2026-03-05 11:00 | 1772726400 | 1 | 0.6111 | 1.33 | 131.91 | 109.76 | 4.316
2026-03-05 12:00 | 1772730000 | 1 | 0.5389 | 1.064 | 148.1 | 116.36 | 4.948
2026-03-05 13:00 | 1772733600 | 1 | 0.3306 | 0.668 | 153.92 | 122.14 | 3.103
2026-03-05 14:00 | 1772737200 | 1 | 0.4056 | 0.912 | 150.58 | 113.37 | 4.97
2026-03-05 15:00 | 1772740800 | 1 | 0.3972 | 0.796 | 147.21 | 117.1 | 3.51
2026-03-05 16:00 | 1772744400 | 1 | 0.3972 | 0.893 | 151.63 | 118.23 | 4.371
2026-03-05 17:00 | 1772748000 | 1 | 0.5222 | 1.046 | 148.29 | 121.28 | 4.139
2026-03-05 18:00 | 1772751600 | 1 | 0.5306 | 1.161 | 144.64 | 116.1 | 4.858
2026-03-05 19:00 | 1772755200 | 1 | 0.3 | 0.695 | 140.72 | 109.9 | 3.14
2026-03-05 20:00 | 1772758800 | 1 | 0.4444 | 0.857 | 132.53 | 103.09 | 3.699
2026-03-05 21:00 | 1772762400 | 1 | 0.225 | 0.449 | 141.99 | 105.92 | 2.365
2026-03-05 22:00 | 1772766000 | 1 | 0.4889 | 0.937 | 140.5 | 109.64 | 4.238
2026-03-05 23:00 | 1772769600 | 1 | 0.5694 | 1.154 | 151.94 | 120.52 | 5.303
2026-03-06 00:00 | 1772773200 | 1 | 0.5528 | 1.113 | 152.8 | 126.15 | 4.345
2026-03-06 01:00 | 1772776800 | 1 | 0.6361 | 1.397 | 146.5 | 119.57 | 5.478
2026-03-06 02:00 | 1772780400 | 1 | 0.5778 | 1.165 | 142.59 | 122.28 | 3.466
2026-03-06 03:00 | 1772784000 | 1 | 0.7167 | 1.542 | 143.28 | 119.64 | 5.343
2026-03-06 04:00 | 1772787600 | 1 | 0.6611 | 1.287 | 150.09 | 122.21 | 5.26
2026-03-06 05:00 | 1772791200 | 1 | 0.65 | 1.319 | 141.3 | 116.85 | 4.726
2026-03-06 06:00 | 1772794800 | 1 | 0.6333 | 1.271 | 145.74 | 123.48 | 4.147
2026-03-06 07:00 | 1772798400 | 1 | 0.6083 | 1.302 | 149.33 | 120.37 | 5.522
2026-03-06 08:00 | 1772802000 | 1 | 0.525 | 1.091 | 147.31 | 116.67 | 4.9
2026-03-06 09:00 | 1772805600 | 1 | 0.4389 | 0.878 | 145.49 | 118.28 | 3.501
2026-03-06 10:00 | 1772809200 | 1 | 0.5361 | 1.035 | 142.06 | 115.19 | 4.072
2026-03-06 11:00 | 1772812800 | 1 | 0.4639 | 0.926 | 142.82 | 117.54 | 3.429
2026-03-06 12:00 | 1772816400 | 1 | 0.5833 | 1.172 | 128.2 | 106.97 | 3.646
2026-03-06 13:00 | 1772820000 | 1 | 0.475 | 0.956 | 129.72 | 109.56 | 2.82
2026-03-06 14:00 | 1772823600 | 1 | 0.55 | 1.097 | 128.89 | 106.08 | 3.664
2026-03-06 15:00 | 1772827200 | 1 | 0.3667 | 0.739 | 133.38 | 110.92 | 2.43
2026-03-06 16:00 | 1772830800 | 1 | 0.45 | 0.864 | 147.32 | 112.56 | 4.4
2026-03-06 17:00 | 1772834400 | 1 | 0.2222 | 0.446 | 140.9 | 106.94 | 2.218
2026-03-06 18:00 | 1772838000 | 1 | 0.2917 | 0.597 | 138.93 | 103.54 | 3.096
2026-03-06 19:00 | 1772841600 | 1 | 0.3667 | 0.734 | 135.21 | 107.89 | 2.937
2026-03-06 20:00 | 1772845200 | 1 | 0.3222 | 0.716 | 130.49 | 100.19 | 3.179
2026-03-06 21:00 | 1772848800 | 1 | 0.4167 | 0.794 | 138.47 | 107.19 | 3.64
2026-03-06 22:00 | 1772852400 | 1 | 0.4028 | 0.806 | 140.41 | 113.02 | 3.233
2026-03-06 23:00 | 1772856000 | 1 | 0.4722 | 1.05 | 138.31 | 111.52 | 4.121
2026-03-07 00:00 | 1772859600 | 1 | 0.5778 | 1.159 | 139.03 | 115.66 | 3.971
2026-03-07 01:00 | 1772863200 | 1 | 0.6806 | 1.37 | 126.95 | 111.73 | 3.054
2026-03-07 02:00 | 1772866800 | 1 | 0.6 | 1.269 | 146.6 | 118.96 | 5.141
2026-03-07 03:00 | 1772870400 | 1 | 0.4611 | 0.921 | 143.64 | 119.48 | 3.259
2026-03-07 04:00 | 1772874000 | 1 | 0.6 | 1.245 | 137.17 | 112.6 | 4.484
2026-03-07 05:00 | 1772877600 | 1 | 0.5 | 1.033 | 144.41 | 115.28 | 4.409
2026-03-07 06:00 | 1772881200 | 1 | 0.3528 | 0.708 | 141.95 | 114.76 | 2.82
2026-03-07 07:00 | 1772884800 | 1 | 0.4639 | 0.923 | 139.12 | 110.99 | 3.791
2026-03-07 08:00 | 1772888400 | 1 | 0.4722 | 0.948 | 136.76 | 113.63 | 3.214
2026-03-07 09:00 | 1772892000 | 1 | 0.5444 | 1.054 | 122.18 | 102.65 | 3.015
2026-03-07 10:00 | 1772895600 | 1 | 0.5722 | 1.221 | 132.1 | 109.38 | 4.065
2026-03-07 11:00 | 1772899200 | 1 | 0.375 | 0.753 | 145.82 | 115.14 | 3.379
2026-03-07 12:00 | 1772902800 | 1 | 0.3167 | 0.596 | 125.37 | 98.95 | 2.307
2026-03-07 13:00 | 1772906400 | 1 | 0.3694 | 0.841 | 126.98 | 100.66 | 3.244
2026-03-07 14:00 | 1772910000 | 1 | 0.4056 | 0.804 | 133.73 | 110.48 | 2.738
2026-03-07 15:00 | 1772913600 | 1 | 0.4694 | 0.926 | 131.23 | 106.86 | 3.308
2026-03-07 16:00 | 1772917200 | 1 | 0.4472 | 0.993 | 125.83 | 102.77 | 3.355
2026-03-07 17:00 | 1772920800 | 1 | 0.4444 | 0.894 | 128.38 | 107.17 | 2.78
2026-03-07 18:00 | 1772924400 | 1 | 0.4139 | 0.884 | 136.44 | 109.21 | 3.527
2026-03-07 19:00 | 1772928000 | 1 | 0.6056 | 1.184 | 119.13 | 102.11 | 2.951
2026-03-07 20:00 | 1772931600 | 1 | 0.725 | 1.445 | 113.85 | 99.87 | 2.962
2026-03-07 21:00 | 1772935200 | 1 | 0.825 | 1.723 | 129.09 | 113.03 | 4.057
2026-03-07 22:00 | 1772938800 | 1 | 0.7 | 1.408 | 136.07 | 116.6 | 4.01
2026-03-07 23:00 | 1772942400 | 1 | 0.5944 | 1.127 | 132.35 | 111.01 | 3.523
2026-03-08 00:00 | 1772946000 | 1 | 0.4639 | 0.975 | 132.53 | 108.65 | 3.412
2026-03-08 01:00 | 1772949600 | 1 | 0.3861 | 0.779 | 131.36 | 107.42 | 2.73
2026-03-08 03:00 | 1772953200 | 1 | 0.3833 | 0.729 | 127.23 | 103.51 | 2.53
2026-03-08 04:00 | 1772956800 | 1 | 0.3889 | 0.781 | 134.64 | 109.39 | 2.887
2026-03-08 05:00 | 1772960400 | 1 | 0.4333 | 0.832 | 115.83 | 97.09 | 2.284
2026-03-08 06:00 | 1772964000 | 1 | 0.3889 | 0.876 | 129.53 | 104.33 | 3.236
2026-03-08 07:00 | 1772967600 | 1 | 0.3333 | 0.731 | 136.89 | 103.4 | 3.583
2026-03-08 08:00 | 1772971200 | 1 | 0.2861 | 0.577 | 113.55 | 99.11 | 1.22
2026-03-08 09:00 | 1772974800 | 1 | 0.5861 | 1.281 | 109.4 | 94.24 | 2.846
2026-03-08 10:00 | 1772978400 | 1 | 0.4083 | 0.817 | 127.03 | 107.32 | 2.359
2026-03-08 11:00 | 1772982000 | 1 | 0.3833 | 0.869 | 101.26 | 88.26 | 1.649
2026-03-08 12:00 | 1772985600 | 1 | 0.1417 | 0.289 | 99.95 | 86.44 | 0.567
2026-03-08 13:00 | 1772989200 | 1 | 0 | 0 |  |  | 0
2026-03-08 14:00 | 1772992800 | 1 | 0 | 0 |  |  | 0
2026-03-08 15:00 | 1772996400 | 1 | 0.0778 | 0.159 | 130.13 | 75.63 | 1.272
2026-03-08 16:00 | 1773000000 | 1 | 0 | 0 |  |  | 0
2026-03-08 17:00 | 1773003600 | 1 | 0.0778 | 0.156 | 119.57 | 77.62 | 0.959
2026-03-08 18:00 | 1773007200 | 1 | 0.0833 | 0.167 | 125.8 | 86.17 | 0.968
2026-03-08 19:00 | 1773010800 | 1 | 0.0833 | 0.168 | 131.07 | 80.57 | 1.246
2026-03-08 20:00 | 1773014400 | 1 | 0.075 | 0.114 | 137.32 | 80.5 | 0.945
2026-03-08 21:00 | 1773018000 | 1 | 0.0833 | 0.169 | 136.4 | 81.89 | 1.348
2026-03-08 22:00 | 1773021600 | 1 | 0.1944 | 0.39 | 141.25 | 98.46 | 2.445
2026-03-08 23:00 | 1773025200 | 1 | 0.2417 | 0.444 | 139.33 | 95.57 | 2.846
2026-03-09 00:00 | 1773028800 | 1 | 0.2333 | 0.467 | 137.39 | 104.29 | 2.265
2026-03-09 01:00 | 1773032400 | 1 | 0.3111 | 0.584 | 137.7 | 102.54 | 3.01
2026-03-09 02:00 | 1773036000 | 1 | 0.1028 | 0.205 | 145.72 | 103.94 | 1.253
2026-03-09 03:00 | 1773039600 | 1 | 0.2667 | 0.496 | 146.49 | 98.81 | 3.465
2026-03-09 04:00 | 1773043200 | 1 | 0.1833 | 0.367 | 146.01 | 100.9 | 2.427
2026-03-09 05:00 | 1773046800 | 1 | 0.1361 | 0.311 | 146.81 | 96.88 | 2.274
2026-03-09 06:00 | 1773050400 | 1 | 0.1944 | 0.39 | 140.34 | 102.37 | 2.169
2026-03-09 07:00 | 1773054000 | 1 | 0.2861 | 0.539 | 138.21 | 100.16 | 2.993
2026-03-09 08:00 | 1773057600 | 1 | 0.1917 | 0.384 | 132.94 | 95.51 | 2.106
2026-03-09 09:00 | 1773061200 | 1 | 0.1806 | 0.321 | 132.23 | 92.1 | 1.884
2026-03-09 10:00 | 1773064800 | 1 | 0.225 | 0.456 | 129.61 | 97.11 | 2.17
2026-03-09 11:00 | 1773068400 | 1 | 0.2 | 0.405 | 130.15 | 100.49 | 1.752
2026-03-09 12:00 | 1773072000 | 1 | 0.2611 | 0.484 | 129.96 | 93.22 | 2.606
2026-03-09 13:00 | 1773075600 | 1 | 0.1417 | 0.286 | 124.09 | 89.04 | 1.467
2026-03-09 14:00 | 1773079200 | 0.9528 | 0.3557 | 0.712 | 117.76 | 90.46 | 2.713
2026-03-09 15:00 | 1773082800 | 1 | 0.1806 | 0.36 | 113.9 | 90.73 | 1.221
2026-03-09 16:00 | 1773086400 | 1 | 0.1333 | 0.267 | 145.95 | 103.42 | 1.662
2026-03-09 17:00 | 1773090000 | 1 | 0.0861 | 0.175 | 151.02 | 98.12 | 1.353
2026-03-09 18:00 | 1773093600 | 1 | 0.0833 | 0.166 | 144.3 | 89.44 | 1.336
2026-03-09 19:00 | 1773097200 | 1 | 0.2639 | 0.547 | 147.48 | 100.01 | 3.806
2026-03-09 20:00 | 1773100800 | 1 | 0.0556 | 0.114 | 139.74 | 84.71 | 0.923
2026-03-09 21:00 | 1773104400 | 1 | 0.0722 | 0.145 | 139.07 | 90.29 | 1.039
2026-03-09 22:00 | 1773108000 | 1 | 0.1333 | 0.268 | 139.53 | 98.98 | 1.591
2026-03-09 23:00 | 1773111600 | 1 | 0.2056 | 0.412 | 140.64 | 102.44 | 2.307
2026-03-10 00:00 | 1773115200 | 1 | 0.2194 | 0.528 | 127.12 | 96.57 | 2.363
2026-03-10 01:00 | 1773118800 | 1 | 0.3389 | 0.682 | 126.34 | 102.42 | 2.389
2026-03-10 02:00 | 1773122400 | 1 | 0.2833 | 0.572 | 124.78 | 102.32 | 1.882
2026-03-10 03:00 | 1773126000 | 1 | 0.3778 | 0.829 | 123.36 | 99.9 | 2.838
2026-03-10 04:00 | 1773129600 | 1 | 0.35 | 0.703 | 129.69 | 104.62 | 2.582
2026-03-10 05:00 | 1773133200 | 1 | 0.2333 | 0.424 | 128.45 | 100.88 | 1.714
2026-03-10 06:00 | 1773136800 | 1 | 0.1472 | 0.295 | 121.3 | 86.29 | 1.511
2026-03-10 07:00 | 1773140400 | 1 | 0.2 | 0.366 | 124.51 | 90 | 1.84
2026-03-10 08:00 | 1773144000 | 1 | 0.1944 | 0.39 | 124.57 | 92.82 | 1.816
2026-03-10 09:00 | 1773147600 | 1 | 0.2806 | 0.521 | 123.54 | 92.27 | 2.388
2026-03-10 10:00 | 1773151200 | 1 | 0.225 | 0.455 | 109.27 | 91.77 | 1.16
2026-03-10 11:00 | 1773154800 | 1 | 0.1056 | 0.215 | 104.19 | 86.93 | 0.544
2026-03-10 12:00 | 1773158400 | 1 | 0 | 0 |  |  | 0
2026-03-10 13:00 | 1773162000 | 1 | 0 | 0.004 |  |  | 0.004
2026-03-10 14:00 | 1773165600 | 1 | 0 | 0 |  |  | 0
2026-03-10 15:00 | 1773169200 | 1 | 0 | 0 |  |  | 0
2026-03-10 16:00 | 1773172800 | 1 | 0 | 0 |  |  | 0
2026-03-10 17:00 | 1773176400 | 1 | 0 | 0 |  |  | 0
2026-03-10 18:00 | 1773180000 | 1 | 0 | 0 |  |  | 0
2026-03-10 19:00 | 1773183600 | 1 | 0 | 0 |  |  | 0
2026-03-10 20:00 | 1773187200 | 1 | 0 | 0 |  |  | 0
2026-03-10 21:00 | 1773190800 | 1 | 0 | 0 |  |  | 0
2026-03-10 22:00 | 1773194400 | 1 | 0 | 0 |  |  | 0
2026-03-10 23:00 | 1773198000 | 1 | 0 | 0 |  |  | 0
2026-03-11 00:00 | 1773201600 | 0.9972 | 0.078 | 0.157 | 133.72 | 78.92 | 1.255
2026-03-11 01:00 | 1773205200 | 1 | 0.0833 | 0.167 | 162.4 | 90.04 | 1.774
2026-03-11 02:00 | 1773208800 | 1 | 0.0833 | 0.167 | 154.6 | 91.43 | 1.55
2026-03-11 03:00 | 1773212400 | 1 | 0.1611 | 0.287 | 148.05 | 92.11 | 2.351
2026-03-11 04:00 | 1773216000 | 1 | 0.0889 | 0.174 | 153.84 | 96.03 | 1.473
2026-03-11 05:00 | 1773219600 | 1 | 0.1639 | 0.292 | 151 | 93.07 | 2.481
2026-03-11 06:00 | 1773223200 | 1 | 0.175 | 0.359 | 151.1 | 97.95 | 2.794
2026-03-11 07:00 | 1773226800 | 1 | 0.1028 | 0.208 | 145.67 | 101.16 | 1.35
2026-03-11 08:00 | 1773230400 | 1 | 0.2167 | 0.396 | 143.22 | 97.47 | 2.655
2026-03-11 09:00 | 1773234000 | 1 | 0.175 | 0.352 | 142.99 | 101.46 | 2.141
2026-03-11 10:00 | 1773237600 | 1 | 0.1194 | 0.225 | 139.72 | 92.68 | 1.562
2026-03-11 11:00 | 1773241200 | 1 | 0.2028 | 0.367 | 141.34 | 88.99 | 2.804
2026-03-11 12:00 | 1773244800 | 1 | 0.15 | 0.311 | 131.12 | 95.23 | 1.634
2026-03-11 13:00 | 1773248400 | 1 | 0.6361 | 1.37 | 140.26 | 116.58 | 4.754
2026-03-11 14:00 | 1773252000 | 1 | 0.775 | 1.551 | 134.51 | 118.89 | 3.55
2026-03-11 15:00 | 1773255600 | 1 | 0.5917 | 1.211 | 139.95 | 116.31 | 4.196
2026-03-11 16:00 | 1773259200 | 1 | 0.4389 | 0.881 | 135.38 | 112.61 | 2.939
2026-03-11 17:00 | 1773262800 | 1 | 0.2111 | 0.425 | 135.04 | 103.93 | 1.937
2026-03-11 18:00 | 1773266400 | 1 | 0.275 | 0.551 | 142.78 | 105.89 | 2.98
2026-03-11 19:00 | 1773270000 | 1 | 0.4278 | 0.953 | 138.58 | 109.43 | 4.071
2026-03-11 20:00 | 1773273600 | 1 | 0.3139 | 0.635 | 135.6 | 111.4 | 2.247
2026-03-11 21:00 | 1773277200 | 1 | 0.625 | 1.264 | 128.8 | 109.1 | 3.648
2026-03-11 22:00 | 1773280800 | 1 | 0.7694 | 1.5 | 130.92 | 112.94 | 3.952
2026-03-11 23:00 | 1773284400 | 1 | 0.75 | 1.503 | 131.49 | 115.41 | 3.54
2026-03-12 00:00 | 1773288000 | 1 | 0.7444 | 1.513 | 126.53 | 113.43 | 2.904
2026-03-12 01:00 | 1773291600 | 1 | 0.8889 | 1.816 | 114.6 | 104.73 | 2.625
2026-03-12 02:00 | 1773295200 | 1 | 0.8528 | 1.798 | 132.45 | 114.17 | 4.816
2026-03-12 04:00 | 1773302400 | 1 | 0.7611 | 1.512 | 128.24 | 110.83 | 3.858
2026-03-12 05:00 | 1773306000 | 1 | 0.5056 | 1.022 | 127.87 | 110.8 | 2.553
2026-03-12 06:00 | 1773309600 | 1 | 0.5861 | 1.164 | 132.42 | 111.97 | 3.487
2026-03-12 07:00 | 1773313200 | 1 | 0.4444 | 0.886 | 144.81 | 117.98 | 3.484
2026-03-12 08:00 | 1773316800 | 1 | 0.3417 | 0.777 | 142.07 | 107.8 | 3.9
2026-03-12 09:00 | 1773320400 | 1 | 0.2917 | 0.579 | 141.04 | 113.47 | 2.34
2026-03-12 10:00 | 1773324000 | 1 | 0.3611 | 0.724 | 140.33 | 111.19 | 3.092
2026-03-12 11:00 | 1773327600 | 1 | 0.3222 | 0.666 | 132.15 | 108.9 | 2.269
2026-03-12 12:00 | 1773331200 | 1 | 0.3083 | 0.616 | 126.1 | 107.41 | 1.689
2026-03-12 13:00 | 1773334800 | 1 | 0.0944 | 0.189 | 127.29 | 93.27 | 0.94
2026-03-12 14:00 | 1773338400 | 1 | 0.2222 | 0.416 | 134.97 | 88.49 | 2.837
2026-03-12 15:00 | 1773342000 | 1 | 0.1083 | 0.216 | 140.09 | 95.99 | 1.399
2026-03-12 16:00 | 1773345600 | 1 | 0.0889 | 0.178 | 151.85 | 98.93 | 1.384
2026-03-12 17:00 | 1773349200 | 1 | 0.225 | 0.442 | 151.8 | 103.1 | 3.164
2026-03-12 18:00 | 1773352800 | 1 | 0.3056 | 0.57 | 146.43 | 105.97 | 3.378
2026-03-12 19:00 | 1773356400 | 1 | 0.3361 | 0.671 | 141.34 | 109.89 | 3.094
2026-03-12 20:00 | 1773360000 | 1 | 0.3944 | 0.748 | 137.54 | 108.86 | 3.144
2026-03-12 21:00 | 1773363600 | 1 | 0.4556 | 1.008 | 137.76 | 108.66 | 4.296
2026-03-12 22:00 | 1773367200 | 1 | 0.3361 | 0.677 | 148.5 | 115.63 | 3.262
2026-03-12 23:00 | 1773370800 | 1 | 0.4139 | 0.787 | 152.34 | 115.19 | 4.285
2026-03-13 00:00 | 1773374400 | 1 | 0.4472 | 0.894 | 137.64 | 111.91 | 3.373
2026-03-13 01:00 | 1773378000 | 1 | 0.5 | 1.064 | 155.85 | 124.16 | 4.941
2026-03-13 02:00 | 1773381600 | 1 | 0.5611 | 1.117 | 158.37 | 129.37 | 4.745
2026-03-13 03:00 | 1773385200 | 1 | 0.5194 | 1.128 | 155.16 | 122.36 | 5.422
2026-03-13 04:00 | 1773388800 | 1 | 0.4944 | 0.986 | 149.41 | 123.18 | 3.791
2026-03-13 05:00 | 1773392400 | 1 | 0.4417 | 0.966 | 163.81 | 127.53 | 5.137
2026-03-13 06:00 | 1773396000 | 1 | 0.4361 | 0.965 | 163.54 | 122.34 | 5.826
2026-03-13 07:00 | 1773399600 | 1 | 0.2806 | 0.564 | 166.15 | 126.99 | 3.222
2026-03-13 08:00 | 1773403200 | 1 | 0.2389 | 0.477 | 162.16 | 119.75 | 2.961
2026-03-13 09:00 | 1773406800 | 1 | 0.3556 | 0.676 | 160.9 | 112.09 | 4.833
2026-03-13 10:00 | 1773410400 | 1 | 0.2389 | 0.477 | 158.42 | 113.27 | 3.157
2026-03-13 11:00 | 1773414000 | 1 | 0.1389 | 0.236 | 156.16 | 99.12 | 1.972
2026-03-13 12:00 | 1773417600 | 1 | 0.0694 | 0.138 | 136.97 | 99.14 | 0.766
2026-03-13 13:00 | 1773421200 | 1 | 0.0889 | 0.177 | 164.98 | 94.35 | 1.829
2026-03-13 14:00 | 1773424800 | 1 | 0.0833 | 0.166 | 150.73 | 92.31 | 1.42
2026-03-13 15:00 | 1773428400 | 1 | 0.0889 | 0.179 | 152.54 | 92.29 | 1.577
2026-03-13 16:00 | 1773432000 | 1 | 0.1861 | 0.375 | 151.89 | 99.73 | 2.858
2026-03-13 17:00 | 1773435600 | 1 | 0.2222 | 0.448 | 150.72 | 109.11 | 2.73
2026-03-13 18:00 | 1773439200 | 1 | 0.2611 | 0.545 | 147.72 | 103.51 | 3.533
2026-03-13 19:00 | 1773442800 | 1 | 0.2222 | 0.446 | 142.47 | 107.17 | 2.304
2026-03-13 20:00 | 1773446400 | 1 | 0.2694 | 0.539 | 139.27 | 108.57 | 2.425
2026-03-13 21:00 | 1773450000 | 1 | 0.4083 | 0.925 | 141.66 | 110.19 | 4.249
2026-03-13 22:00 | 1773453600 | 1 | 0.2222 | 0.449 | 142.7 | 109.09 | 2.202
2026-03-13 23:00 | 1773457200 | 1 | 0.2167 | 0.519 | 147.94 | 100.67 | 3.595
2026-03-14 00:00 | 1773460800 | 1 | 0.2444 | 0.488 | 148.01 | 112.39 | 2.548
2026-03-14 01:00 | 1773464400 | 1 | 0.4972 | 1.049 | 144.98 | 111.27 | 5.185
2026-03-14 03:00 | 1773471600 | 1 | 0.5861 | 1.143 | 138.8 | 114.74 | 4.023
2026-03-14 04:00 | 1773475200 | 1 | 0.3778 | 0.756 | 138.26 | 117.15 | 2.337
2026-03-14 05:00 | 1773478800 | 1 | 0.2806 | 0.528 | 140.08 | 99.15 | 3.166
2026-03-14 06:00 | 1773482400 | 1 | 0.2389 | 0.479 | 138.71 | 107.46 | 2.191
2026-03-14 07:00 | 1773486000 | 1 | 0.2778 | 0.63 | 137.07 | 104.24 | 3.03
2026-03-14 08:00 | 1773489600 | 1 | 0.4417 | 0.862 | 133.64 | 107.31 | 3.325
2026-03-14 09:00 | 1773493200 | 1 | 0.4472 | 0.885 | 131.38 | 107.25 | 3.129
2026-03-14 10:00 | 1773496800 | 1 | 0.1472 | 0.263 | 133.84 | 108.41 | 0.981
2026-03-14 11:00 | 1773500400 | 1 | 0.1611 | 0.283 | 127.03 | 85.3 | 1.73
2026-03-14 12:00 | 1773504000 | 1 | 0.0833 | 0.143 | 134.8 | 83.28 | 1.08
2026-03-14 13:00 | 1773507600 | 1 | 0.2222 | 0.441 | 139.17 | 101.58 | 2.431
2026-03-14 14:00 | 1773511200 | 1 | 0.2028 | 0.41 | 133.24 | 98.98 | 2.059
2026-03-14 15:00 | 1773514800 | 1 | 0.2611 | 0.522 | 138.88 | 97.86 | 3.133
2026-03-14 16:00 | 1773518400 | 1 | 0.2083 | 0.421 | 144.44 | 104.2 | 2.475
2026-03-14 17:00 | 1773522000 | 1 | 0.1889 | 0.339 | 145.95 | 99.27 | 2.316
2026-03-14 18:00 | 1773525600 | 1 | 0.0889 | 0.178 | 141.62 | 99.6 | 1.098
2026-03-14 19:00 | 1773529200 | 1 | 0.1694 | 0.291 | 134.5 | 86 | 2.066
2026-03-14 20:00 | 1773532800 | 1 | 0.1 | 0.2 | 144.68 | 99.18 | 1.335
2026-03-14 21:00 | 1773536400 | 1 | 0.2028 | 0.48 | 132.65 | 91.58 | 2.885
2026-03-14 22:00 | 1773540000 | 1 | 0.325 | 0.611 | 143.01 | 102.67 | 3.609
2026-03-14 23:00 | 1773543600 | 1 | 0.2306 | 0.468 | 149.52 | 110.75 | 2.645
2026-03-15 00:00 | 1773547200 | 1 | 0.3694 | 0.709 | 141.04 | 104.8 | 3.767
2026-03-15 01:00 | 1773550800 | 0.9556 | 0.4564 | 0.917 | 135.13 | 107.15 | 3.595
2026-03-15 02:00 | 1773554400 | 1 | 0.5889 | 1.284 | 139.85 | 112.56 | 5.135
2026-03-15 03:00 | 1773558000 | 1 | 0.3083 | 0.616 | 150.56 | 119.15 | 2.833
2026-03-15 04:00 | 1773561600 | 1 | 0.3861 | 0.872 | 147.37 | 113.06 | 4.385
2026-03-15 05:00 | 1773565200 | 1 | 0.4083 | 0.92 | 145.94 | 112.38 | 4.523
2026-03-15 06:00 | 1773568800 | 1 | 0.3889 | 0.78 | 142.44 | 117.72 | 2.827
2026-03-15 07:00 | 1773572400 | 1 | 0.4528 | 1.01 | 139.59 | 112.29 | 4.033
2026-03-15 08:00 | 1773576000 | 1 | 0.5194 | 1.122 | 133.17 | 108.05 | 4.128
2026-03-15 09:00 | 1773579600 | 1 | 0.2889 | 0.581 | 139.83 | 112.69 | 2.306
2026-03-15 10:00 | 1773583200 | 1 | 0.2722 | 0.506 | 139.38 | 98.15 | 3.057
2026-03-15 11:00 | 1773586800 | 1 | 0 | 0 |  |  | 0
2026-03-15 12:00 | 1773590400 | 1 | 0.0778 | 0.117 | 133.67 | 80.99 | 0.902
2026-03-15 13:00 | 1773594000 | 1 | 0 | 0 |  |  | 0
2026-03-15 14:00 | 1773597600 | 1 | 0 | 0 |  |  | 0
2026-03-15 15:00 | 1773601200 | 1 | 0 | 0 |  |  | 0
2026-03-15 16:00 | 1773604800 | 1 | 0.0528 | 0.106 | 128.24 | 66.26 | 0.959
2026-03-15 17:00 | 1773608400 | 1 | 0.1222 | 0.245 | 137.33 | 90.97 | 1.666
2026-03-15 18:00 | 1773612000 | 1 | 0.2694 | 0.58 | 144.68 | 101.16 | 3.697
2026-03-15 19:00 | 1773615600 | 1 | 0.3 | 0.606 | 142.88 | 108.31 | 3.061
2026-03-15 20:00 | 1773619200 | 1 | 0.275 | 0.641 | 137.45 | 102.97 | 3.239
2026-03-15 21:00 | 1773622800 | 1 | 0.0972 | 0.195 | 135.33 | 101.7 | 0.961
2026-03-15 22:00 | 1773626400 | 1 | 0.2667 | 0.498 | 127.1 | 90.69 | 2.657
2026-03-15 23:00 | 1773630000 | 1 | 0.2139 | 0.429 | 135.05 | 100.59 | 2.167
2026-03-16 00:00 | 1773633600 | 1 | 0.2833 | 0.585 | 136.93 | 104.08 | 2.815
2026-03-16 01:00 | 1773637200 | 1 | 0.3639 | 0.729 | 143.82 | 111.03 | 3.504
2026-03-16 02:00 | 1773640800 | 1 | 0.3194 | 0.599 | 140.22 | 105.99 | 3.002
2026-03-16 03:00 | 1773644400 | 1 | 0.3722 | 0.748 | 135.04 | 109.36 | 2.814
2026-03-16 04:00 | 1773648000 | 1 | 0.45 | 0.864 | 132.63 | 105.61 | 3.42
2026-03-16 05:00 | 1773651600 | 1 | 0.3167 | 0.732 | 144.93 | 110.25 | 3.714
2026-03-16 06:00 | 1773655200 | 1 | 0.3389 | 0.681 | 144.39 | 111.72 | 3.256
2026-03-16 07:00 | 1773658800 | 1 | 0.2806 | 0.527 | 144.46 | 104.17 | 3.108
2026-03-16 08:00 | 1773662400 | 1 | 0.1 | 0.201 | 141.82 | 104.78 | 1.089
2026-03-16 09:00 | 1773666000 | 1 | 0.2583 | 0.503 | 138.51 | 95.58 | 3.156
2026-03-16 10:00 | 1773669600 | 1 | 0.2111 | 0.423 | 137.13 | 102.11 | 2.172
2026-03-16 11:00 | 1773673200 | 1 | 0.2972 | 0.555 | 136.4 | 100.72 | 2.901
2026-03-16 12:00 | 1773676800 | 1 | 0.3472 | 0.7 | 128.86 | 104.65 | 2.482
2026-03-16 13:00 | 1773680400 | 1 | 0.2861 | 0.575 | 135.76 | 101.21 | 2.907
2026-03-16 14:00 | 1773684000 | 1 | 0.2389 | 0.478 | 132.44 | 101.48 | 2.169
2026-03-16 15:00 | 1773687600 | 1 | 0.2583 | 0.521 | 133.03 | 101.76 | 2.39
2026-03-16 16:00 | 1773691200 | 1 | 0.3 | 0.583 | 131.69 | 99.29 | 2.764
2026-03-16 17:00 | 1773694800 | 1 | 0.2444 | 0.491 | 130.63 | 103.12 | 1.977
2026-03-16 18:00 | 1773698400 | 1 | 0.7722 | 1.579 | 110.66 | 101.08 | 2.218
2026-03-16 19:00 | 1773702000 | 1 | 1 | 2.075 | 99.81 | 93.19 | 2.014
2026-03-16 20:00 | 1773705600 | 1 | 1 | 2.005 | 123.82 | 110.49 | 3.919
2026-03-16 21:00 | 1773709200 | 1 | 0.825 | 1.613 | 123.42 | 111.64 | 2.785
2026-03-16 22:00 | 1773712800 | 1 | 0.2028 | 0.406 | 116.13 | 96.15 | 1.188
2026-03-16 23:00 | 1773716400 | 1 | 0.2056 | 0.416 | 113.87 | 91.58 | 1.352
2026-03-17 00:00 | 1773720000 | 1 | 0.275 | 0.547 | 108.53 | 90.2 | 1.469
2026-03-17 01:00 | 1773723600 | 1 | 0.3972 | 0.807 | 105.13 | 88.78 | 1.93
2026-03-17 02:00 | 1773727200 | 1 | 0.2417 | 0.483 | 125.25 | 101.39 | 1.687
2026-03-17 03:00 | 1773730800 | 1 | 0.1972 | 0.399 | 120.66 | 96.69 | 1.384
2026-03-17 04:00 | 1773734400 | 1 | 0.1139 | 0.266 | 136.92 | 89.07 | 1.868
2026-03-17 05:00 | 1773738000 | 1 | 0.0972 | 0.194 | 138.56 | 90.62 | 1.363
2026-03-17 06:00 | 1773741600 | 1 | 0.0694 | 0.138 | 147.39 | 93.15 | 1.098
2026-03-17 07:00 | 1773745200 | 1 | 0.0083 | 0.017 | 104.95 | 74.91 | 0.073
2026-03-17 08:00 | 1773748800 | 1 | 0.0694 | 0.139 | 137.14 | 82.53 | 1.111
2026-03-17 09:00 | 1773752400 | 1 | 0.0833 | 0.167 | 133.04 | 84.2 | 1.196
2026-03-17 10:00 | 1773756000 | 1 | 0.1472 | 0.261 | 135.99 | 85.24 | 1.943
2026-03-17 11:00 | 1773759600 | 1 | 0 | 0 |  |  | 0
2026-03-17 12:00 | 1773763200 | 1 | 0.0806 | 0.161 | 134.74 | 84.35 | 1.191
2026-03-17 13:00 | 1773766800 | 1 | 0.0833 | 0.167 | 140.41 | 89.57 | 1.247
2026-03-17 14:00 | 1773770400 | 1 | 0.0833 | 0.167 | 138.3 | 87.71 | 1.238
2026-03-17 15:00 | 1773774000 | 1 | 0.0833 | 0.169 | 145.85 | 89.97 | 1.378
2026-03-17 16:00 | 1773777600 | 1 | 0.1417 | 0.279 | 151.58 | 90.94 | 2.483
2026-03-17 17:00 | 1773781200 | 1 | 0.0889 | 0.178 | 147.56 | 96.15 | 1.341
2026-03-17 18:00 | 1773784800 | 1 | 0.0833 | 0.168 | 142.36 | 92.65 | 1.223
2026-03-17 19:00 | 1773788400 | 1 | 0.2611 | 0.486 | 142.13 | 95.46 | 3.322
2026-03-17 20:00 | 1773792000 | 1 | 0.2389 | 0.486 | 144.8 | 108.01 | 2.609
2026-03-17 21:00 | 1773795600 | 1 | 0.2389 | 0.499 | 157.25 | 105.49 | 3.782
2026-03-17 22:00 | 1773799200 | 1 | 0.2306 | 0.543 | 156.84 | 106.4 | 4.015
2026-03-17 23:00 | 1773802800 | 1 | 0.2861 | 0.576 | 153.05 | 117.07 | 3.035
2026-03-18 00:00 | 1773806400 | 0.9972 | 0.4903 | 0.968 | 154.2 | 119.64 | 4.889
2026-03-18 01:00 | 1773810000 | 1 | 0.4389 | 0.879 | 156.03 | 125.12 | 3.974
2026-03-18 02:00 | 1773813600 | 1 | 0.4139 | 0.93 | 157.22 | 118.11 | 5.33
2026-03-18 03:00 | 1773817200 | 1 | 0.3583 | 0.784 | 158.43 | 122.56 | 4.116
2026-03-18 04:00 | 1773820800 | 1 | 0.4556 | 0.905 | 155.43 | 124.78 | 4.065
2026-03-18 05:00 | 1773824400 | 1 | 0.5778 | 1.155 | 158.86 | 123.62 | 5.964
2026-03-18 06:00 | 1773828000 | 1 | 0.4361 | 0.854 | 154.55 | 118.92 | 4.459
2026-03-18 07:00 | 1773831600 | 1 | 0.4528 | 0.901 | 157.99 | 129.49 | 3.763
2026-03-18 08:00 | 1773835200 | 1 | 0.5639 | 1.087 | 151.2 | 119.84 | 4.995
2026-03-18 09:00 | 1773838800 | 1 | 0.4083 | 0.82 | 144.68 | 116.21 | 3.42
2026-03-18 10:00 | 1773842400 | 1 | 0.5333 | 1.161 | 139.24 | 113.85 | 4.313
2026-03-18 11:00 | 1773846000 | 1 | 0.3361 | 0.777 | 134.9 | 107.23 | 3.149
2026-03-18 12:00 | 1773849600 | 1 | 0.2167 | 0.436 | 138.95 | 104.48 | 2.203
2026-03-18 13:00 | 1773853200 | 1 | 0.275 | 0.51 | 152.21 | 102.62 | 3.7
2026-03-18 14:00 | 1773856800 | 1 | 0.0889 | 0.18 | 143.88 | 90.79 | 1.395
2026-03-18 15:00 | 1773860400 | 1 | 0.0833 | 0.166 | 152.63 | 94.97 | 1.403
2026-03-18 16:00 | 1773864000 | 1 | 0.2278 | 0.508 | 152.46 | 105.68 | 3.481
2026-03-18 17:00 | 1773867600 | 1 | 0.3917 | 0.785 | 157.71 | 120.28 | 4.307
2026-03-18 18:00 | 1773871200 | 1 | 0.35 | 0.667 | 151.55 | 110.6 | 4.003
2026-03-18 19:00 | 1773874800 | 1 | 0.2444 | 0.491 | 145.98 | 113.75 | 2.314
2026-03-18 20:00 | 1773878400 | 1 | 0.3 | 0.59 | 141.28 | 105.11 | 3.129
2026-03-18 21:00 | 1773882000 | 1 | 0.2111 | 0.423 | 143.44 | 104.87 | 2.391
2026-03-18 22:00 | 1773885600 | 1 | 0.4833 | 1.026 | 142.72 | 112.23 | 4.583
2026-03-18 23:00 | 1773889200 | 1 | 0.6361 | 1.373 | 140.56 | 116.18 | 4.907
2026-03-19 00:00 | 1773892800 | 1 | 0.6194 | 1.242 | 142.36 | 122.05 | 3.683
2026-03-19 01:00 | 1773896400 | 1 | 0.7194 | 1.516 | 141.75 | 118.49 | 5.167
2026-03-19 02:00 | 1773900000 | 1 | 0.6528 | 1.413 | 146.96 | 121.9 | 5.176
2026-03-19 03:00 | 1773903600 | 1 | 0.6056 | 1.309 | 146.73 | 120.15 | 5.098
2026-03-19 04:00 | 1773907200 | 1 | 0.5806 | 1.164 | 143.22 | 120.14 | 3.936
2026-03-19 05:00 | 1773910800 | 1 | 0.6333 | 1.287 | 147.65 | 122.19 | 4.8
2026-03-19 06:00 | 1773914400 | 1 | 0.6444 | 1.274 | 148.9 | 121.07 | 5.195
2026-03-19 07:00 | 1773918000 | 1 | 0.5861 | 1.172 | 144.29 | 121.41 | 3.927
2026-03-19 08:00 | 1773921600 | 1 | 0.5833 | 1.275 | 137 | 114.97 | 4.115
2026-03-19 09:00 | 1773925200 | 1 | 0.5111 | 1.024 | 132.73 | 114.29 | 2.769
2026-03-19 10:00 | 1773928800 | 1 | 0.7139 | 1.534 | 126.91 | 108.9 | 4.049
2026-03-19 11:00 | 1773932400 | 1 | 0.4639 | 0.892 | 123.37 | 101.51 | 2.857
2026-03-19 12:00 | 1773936000 | 1 | 0.1222 | 0.246 | 133.08 | 99.37 | 1.213
2026-03-19 13:00 | 1773939600 | 1 | 0.2722 | 0.504 | 140.63 | 98.48 | 3.115
2026-03-19 14:00 | 1773943200 | 1 | 0.0833 | 0.166 | 134.29 | 91.12 | 1.053
2026-03-19 15:00 | 1773946800 | 1 | 0.0889 | 0.177 | 147.77 | 90.92 | 1.474
2026-03-19 16:00 | 1773950400 | 1 | 0.2556 | 0.471 | 145.54 | 94.62 | 3.512
2026-03-19 17:00 | 1773954000 | 1 | 0.0944 | 0.189 | 142.84 | 97.27 | 1.265
2026-03-19 18:00 | 1773957600 | 1 | 0.2028 | 0.392 | 141.87 | 95.36 | 2.67
2026-03-19 19:00 | 1773961200 | 1 | 0.1167 | 0.298 | 141.69 | 92.49 | 2.149
2026-03-19 20:00 | 1773964800 | 1 | 0.1778 | 0.355 | 137.48 | 95.31 | 2.193
2026-03-19 21:00 | 1773968400 | 1 | 0.1861 | 0.334 | 138.65 | 95.47 | 2.111
2026-03-19 22:00 | 1773972000 | 1 | 0.3167 | 0.59 | 141.91 | 99.5 | 3.665
2026-03-19 23:00 | 1773975600 | 1 | 0.2972 | 0.598 | 138.5 | 107.61 | 2.705
2026-03-20 00:00 | 1773979200 | 1 | 0.4778 | 0.957 | 135.65 | 109 | 3.737
2026-03-20 01:00 | 1773982800 | 1 | 0.5444 | 1.093 | 140.17 | 120.07 | 3.218
2026-03-20 02:00 | 1773986400 | 1 | 0.5917 | 1.181 | 139.82 | 115.61 | 4.188
2026-03-20 03:00 | 1773990000 | 1 | 0.4444 | 0.945 | 151.17 | 115.27 | 4.974
2026-03-20 04:00 | 1773993600 | 1 | 0.2444 | 0.494 | 149.51 | 116.1 | 2.418
2026-03-20 05:00 | 1773997200 | 1 | 0.4944 | 0.951 | 140.36 | 109.87 | 4.249
2026-03-20 06:00 | 1774000800 | 1 | 0.4167 | 0.833 | 141.11 | 114.91 | 3.2
2026-03-20 07:00 | 1774004400 | 1 | 0.3889 | 0.871 | 139.71 | 109.69 | 3.832
2026-03-20 08:00 | 1774008000 | 1 | 0.2472 | 0.497 | 137.41 | 108.13 | 2.132
2026-03-20 09:00 | 1774011600 | 1 | 0.0889 | 0.177 | 133.81 | 90.53 | 1.125
2026-03-20 10:00 | 1774015200 | 1 | 0.2944 | 0.555 | 135.73 | 98.27 | 3.046
2026-03-20 11:00 | 1774018800 | 1 | 0.2528 | 0.508 | 133.87 | 103.9 | 2.226
2026-03-20 12:00 | 1774022400 | 1 | 0.4083 | 0.916 | 132.26 | 105.35 | 3.612
2026-03-20 13:00 | 1774026000 | 1 | 0.4278 | 0.859 | 130.4 | 108.53 | 2.751
2026-03-20 14:00 | 1774029600 | 1 | 0.4583 | 0.981 | 124.11 | 101.7 | 3.222
2026-03-20 15:00 | 1774033200 | 1 | 0.4528 | 0.918 | 122.48 | 105.76 | 2.245
2026-03-20 16:00 | 1774036800 | 1 | 0.2528 | 0.581 | 122.23 | 95.03 | 2.315
2026-03-20 17:00 | 1774040400 | 1 | 0.2 | 0.4 | 145.15 | 101.96 | 2.533
2026-03-20 18:00 | 1774044000 | 1 | 0.2861 | 0.531 | 138.79 | 99.35 | 3.069
2026-03-20 19:00 | 1774047600 | 1 | 0.0889 | 0.184 | 136.75 | 96.34 | 1.066
2026-03-20 20:00 | 1774051200 | 1 | 0.2778 | 0.515 | 136.55 | 96.66 | 3.008
2026-03-20 21:00 | 1774054800 | 1 | 0.2278 | 0.459 | 138.08 | 106.19 | 2.143
2026-03-20 22:00 | 1774058400 | 1 | 0.2722 | 0.506 | 131.31 | 96.78 | 2.563
2026-03-20 23:00 | 1774062000 | 1 | 0.2056 | 0.411 | 129.02 | 98.59 | 1.832
2026-03-21 00:00 | 1774065600 | 1 | 0.4917 | 1.019 | 129.56 | 104.96 | 3.672
2026-03-21 01:00 | 1774069200 | 1 | 0.6194 | 1.302 | 124.65 | 106.28 | 3.503
2026-03-21 02:00 | 1774072800 | 1 | 0.7444 | 1.495 | 126 | 111.92 | 3.084
2026-03-21 03:00 | 1774076400 | 1 | 0.6639 | 1.425 | 129.44 | 111.43 | 3.761
2026-03-21 04:00 | 1774080000 | 1 | 0.675 | 1.427 | 121.18 | 106.47 | 3.076
2026-03-21 05:00 | 1774083600 | 1 | 0.7167 | 1.466 | 128.46 | 111.5 | 3.644
2026-03-21 06:00 | 1774087200 | 1 | 0.4667 | 1.024 | 136.01 | 111.36 | 3.701
2026-03-21 07:00 | 1774090800 | 1 | 0.3667 | 0.737 | 134.3 | 113.36 | 2.26
2026-03-21 08:00 | 1774094400 | 1 | 0.2639 | 0.49 | 133.87 | 100.88 | 2.358
2026-03-21 09:00 | 1774098000 | 1 | 0.0833 | 0.167 | 138.3 | 89.51 | 1.194
2026-03-21 10:00 | 1774101600 | 1 | 0.2472 | 0.5 | 134.59 | 91.8 | 3.11
2026-03-21 11:00 | 1774105200 | 1 | 0.2 | 0.404 | 139 | 101.11 | 2.233
2026-03-21 12:00 | 1774108800 | 1 | 0.1944 | 0.352 | 136.97 | 99.38 | 1.938
2026-03-21 13:00 | 1774112400 | 1 | 0.0833 | 0.167 | 142.76 | 88.2 | 1.338
2026-03-21 14:00 | 1774116000 | 1 | 0.1639 | 0.284 | 138.9 | 87.53 | 2.136
2026-03-21 15:00 | 1774119600 | 1 | 0.1639 | 0.291 | 138.76 | 89 | 2.12
2026-03-21 16:00 | 1774123200 | 1 | 0.0889 | 0.175 | 140.97 | 92.01 | 1.257
2026-03-21 17:00 | 1774126800 | 1 | 0.1861 | 0.373 | 136.16 | 95.16 | 2.236
2026-03-21 18:00 | 1774130400 | 1 | 0.275 | 0.51 | 136.14 | 97.82 | 2.859
2026-03-21 19:00 | 1774134000 | 1 | 0.2806 | 0.611 | 132.12 | 97.56 | 3.084
2026-03-21 20:00 | 1774137600 | 1 | 0.3472 | 0.674 | 144.89 | 107.4 | 3.697
2026-03-21 21:00 | 1774141200 | 1 | 0.2444 | 0.47 | 145.39 | 105.36 | 2.753
2026-03-21 22:00 | 1774144800 | 1 | 0.2056 | 0.514 | 149.74 | 101.26 | 3.645
2026-03-21 23:00 | 1774148400 | 1 | 0.2167 | 0.462 | 139.13 | 104.71 | 2.332
2026-03-22 00:00 | 1774152000 | 1 | 0.2889 | 0.551 | 142.84 | 103.88 | 3.142
2026-03-22 01:00 | 1774155600 | 1 | 0.2972 | 0.672 | 144.44 | 107.14 | 3.672
2026-03-22 02:00 | 1774159200 | 1 | 0.4111 | 0.88 | 142.07 | 110.54 | 4.063
2026-03-22 03:00 | 1774162800 | 1 | 0.45 | 0.9 | 138.08 | 114.14 | 3.149
2026-03-22 04:00 | 1774166400 | 1 | 0.5083 | 1.125 | 133.42 | 109.24 | 3.983
2026-03-22 05:00 | 1774170000 | 0.9528 | 0.4577 | 0.918 | 139.36 | 109.89 | 3.776
2026-03-22 06:00 | 1774173600 | 1 | 0.3944 | 0.849 | 139.34 | 111.96 | 3.407
2026-03-22 07:00 | 1774177200 | 1 | 0.4583 | 0.912 | 137.22 | 113.27 | 3.199
2026-03-22 08:00 | 1774180800 | 1 | 0.425 | 0.945 | 138.84 | 110.19 | 3.963
2026-03-22 09:00 | 1774184400 | 1 | 0.2861 | 0.679 | 145.34 | 107.54 | 3.749
2026-03-22 10:00 | 1774188000 | 1 | 0.1806 | 0.362 | 146.41 | 109.85 | 1.937
2026-03-22 11:00 | 1774191600 | 1 | 0.3611 | 0.684 | 143.62 | 106.78 | 3.693
2026-03-22 12:00 | 1774195200 | 1 | 0.2333 | 0.465 | 143.91 | 109.72 | 2.327
2026-03-22 13:00 | 1774198800 | 1 | 0.2583 | 0.506 | 142.46 | 98.73 | 3.242
2026-03-22 14:00 | 1774202400 | 1 | 0.0889 | 0.18 | 138.45 | 96.98 | 1.089
2026-03-22 15:00 | 1774206000 | 1 | 0.2528 | 0.484 | 138.67 | 95.35 | 3.073
2026-03-22 16:00 | 1774209600 | 1 | 0.0944 | 0.187 | 148.35 | 98.21 | 1.377
2026-03-22 17:00 | 1774213200 | 1 | 0.1833 | 0.454 | 143.48 | 94.18 | 3.268
2026-03-22 18:00 | 1774216800 | 1 | 0.2083 | 0.497 | 144.48 | 98.02 | 3.386
2026-03-22 19:00 | 1774220400 | 1 | 0.2111 | 0.422 | 146.2 | 106.79 | 2.435
2026-03-22 20:00 | 1774224000 | 1 | 0.3028 | 0.601 | 141.14 | 105.12 | 3.171
2026-03-22 21:00 | 1774227600 | 1 | 0.4611 | 0.923 | 136.71 | 112.55 | 3.265
2026-03-22 22:00 | 1774231200 | 1 | 0.5611 | 1.216 | 132.02 | 110.79 | 3.783
2026-03-22 23:00 | 1774234800 | 1 | 0.7278 | 1.5 | 138.59 | 118.42 | 4.434
2026-03-23 01:00 | 1774242000 | 1 | 0.6278 | 1.356 | 139.98 | 117.31 | 4.505
2026-03-23 02:00 | 1774245600 | 1 | 0.5889 | 1.177 | 139.39 | 117.84 | 3.716
2026-03-23 03:00 | 1774249200 | 1 | 0.4778 | 1.057 | 140.18 | 112.89 | 4.226
2026-03-23 04:00 | 1774252800 | 0.9528 | 0.6443 | 1.286 | 141.52 | 120.05 | 3.855
2026-03-23 05:00 | 1774256400 | 1 | 0.5222 | 1.141 | 140.09 | 114.08 | 4.348
2026-03-23 06:00 | 1774260000 | 1 | 0.4444 | 0.889 | 144.71 | 118.23 | 3.451
2026-03-23 07:00 | 1774263600 | 1 | 0.4944 | 1.031 | 140.43 | 112.6 | 4.204
2026-03-23 08:00 | 1774267200 | 1 | 0.4278 | 0.897 | 135.89 | 111.19 | 3.236
2026-03-23 09:00 | 1774270800 | 1 | 0.4667 | 0.995 | 128.18 | 108.25 | 2.904
2026-03-23 10:00 | 1774274400 | 1 | 0.65 | 1.411 | 121.69 | 105.58 | 3.33
2026-03-23 11:00 | 1774278000 | 1 | 0.6611 | 1.328 | 119.65 | 105.93 | 2.671
2026-03-23 12:00 | 1774281600 | 1 | 0.5111 | 1.084 | 131.52 | 108.49 | 3.659
2026-03-23 13:00 | 1774285200 | 1 | 0.3222 | 0.605 | 139.41 | 106.18 | 2.943
2026-03-23 14:00 | 1774288800 | 1 | 0.1944 | 0.387 | 145.55 | 103.34 | 2.393
2026-03-23 15:00 | 1774292400 | 1 | 0.1722 | 0.306 | 141.17 | 95.34 | 2.05
2026-03-23 16:00 | 1774296000 | 1 | 0.0833 | 0.171 | 136.82 | 86.52 | 1.258
2026-03-23 17:00 | 1774299600 | 1 | 0.0833 | 0.125 | 138.61 | 87.45 | 0.937
2026-03-23 18:00 | 1774303200 | 1 | 0.1722 | 0.344 | 138.34 | 90.88 | 2.389
2026-03-23 19:00 | 1774306800 | 1 | 0.1667 | 0.296 | 139 | 91.46 | 2.059
2026-03-23 20:00 | 1774310400 | 1 | 0.2472 | 0.469 | 137.5 | 95.9 | 2.861
2026-03-23 21:00 | 1774314000 | 1 | 0.2639 | 0.517 | 135.94 | 105.66 | 2.291
2026-03-23 22:00 | 1774317600 | 1 | 0.4472 | 0.966 | 145.96 | 111.84 | 4.828
2026-03-23 23:00 | 1774321200 | 1 | 0.3222 | 0.65 | 145.8 | 115.79 | 2.851
2026-03-24 00:00 | 1774324800 | 1 | 0.4556 | 1.006 | 140.12 | 113.07 | 3.987
2026-03-24 01:00 | 1774328400 | 1 | 0.4556 | 0.911 | 146.92 | 119.52 | 3.656
2026-03-24 02:00 | 1774332000 | 1 | 0.5778 | 1.116 | 145.14 | 116.41 | 4.698
2026-03-24 03:00 | 1774335600 | 1 | 0.4667 | 1.025 | 150.1 | 117.3 | 4.928
2026-03-24 04:00 | 1774339200 | 1 | 0.4333 | 0.866 | 146.91 | 118.76 | 3.573
2026-03-24 05:00 | 1774342800 | 0.9528 | 0.5452 | 1.099 | 144.88 | 122.2 | 3.478
2026-03-24 06:00 | 1774346400 | 1 | 0.6806 | 1.317 | 144.54 | 119.79 | 4.777
2026-03-24 07:00 | 1774350000 | 1 | 0.5944 | 1.188 | 144.45 | 121.28 | 4.029
2026-03-24 08:00 | 1774353600 | 1 | 0.3389 | 0.643 | 142.36 | 109.49 | 3.094
2026-03-24 09:00 | 1774357200 | 1 | 0.2111 | 0.427 | 139.32 | 103 | 2.275
2026-03-24 10:00 | 1774360800 | 1 | 0.2778 | 0.527 | 137.83 | 98.2 | 3.058
2026-03-24 11:00 | 1774364400 | 1 | 0.0889 | 0.178 | 133.3 | 89.61 | 1.138
2026-03-24 12:00 | 1774368000 | 1 | 0.0944 | 0.188 | 143.09 | 95.1 | 1.322
2026-03-24 13:00 | 1774371600 | 1 | 0.0833 | 0.167 | 135.52 | 89.21 | 1.134
2026-03-24 14:00 | 1774375200 | 1 | 0.0889 | 0.179 | 131.41 | 89.37 | 1.104
2026-03-24 15:00 | 1774378800 | 1 | 0.1722 | 0.346 | 143.87 | 92.75 | 2.59
2026-03-24 16:00 | 1774382400 | 1 | 0.0833 | 0.167 | 153.74 | 91.73 | 1.519
2026-03-24 17:00 | 1774386000 | 1 | 0.0889 | 0.18 | 144.41 | 94.97 | 1.306
2026-03-24 18:00 | 1774389600 | 1 | 0.2 | 0.4 | 152.31 | 105.3 | 2.755
2026-03-24 19:00 | 1774393200 | 1 | 0.1722 | 0.314 | 148.05 | 100.33 | 2.191
2026-03-24 20:00 | 1774396800 | 1 | 0.1944 | 0.388 | 145.72 | 103.19 | 2.415
2026-03-24 21:00 | 1774400400 | 1 | 0.2167 | 0.435 | 140.78 | 106.43 | 2.18
2026-03-24 22:00 | 1774404000 | 1 | 0.4444 | 0.857 | 132.8 | 103.64 | 3.653
2026-03-24 23:00 | 1774407600 | 1 | 0.3 | 0.598 | 142.94 | 110.44 | 2.848
2026-03-25 00:00 | 1774411200 | 0.9972 | 0.3872 | 0.736 | 150.84 | 110.94 | 4.293
2026-03-25 01:00 | 1774414800 | 1 | 0.2167 | 0.431 | 153.46 | 111.62 | 2.644
2026-03-25 02:00 | 1774418400 | 1 | 0.2694 | 0.554 | 151.93 | 107.45 | 3.61
2026-03-25 03:00 | 1774422000 | 1 | 0.2389 | 0.483 | 143.11 | 111.47 | 2.226
2026-03-25 04:00 | 1774425600 | 0.9556 | 0.4855 | 1.046 | 131.54 | 103.85 | 4.055
2026-03-25 05:00 | 1774429200 | 1 | 0.3472 | 0.763 | 147.2 | 110.06 | 4.152
2026-03-25 06:00 | 1774432800 | 1 | 0.2944 | 0.59 | 151.25 | 117.95 | 2.878
2026-03-25 07:00 | 1774436400 | 1 | 0.2528 | 0.57 | 152.65 | 109.05 | 3.629
2026-03-25 08:00 | 1774440000 | 1 | 0.2611 | 0.559 | 142.16 | 106.62 | 2.91
2026-03-25 09:00 | 1774443600 | 1 | 0.1667 | 0.39 | 131.91 | 97.7 | 1.956
2026-03-25 10:00 | 1774447200 | 1 | 0.2056 | 0.416 | 129.14 | 97.72 | 1.905
2026-03-25 11:00 | 1774450800 | 1 | 0.1611 | 0.283 | 131.41 | 87.59 | 1.814
2026-03-25 12:00 | 1774454400 | 1 | 0 | 0 |  |  | 0
2026-03-25 13:00 | 1774458000 | 1 | 0.1583 | 0.274 | 153.41 | 86.15 | 2.699
2026-03-25 14:00 | 1774461600 | 1 | 0.0889 | 0.179 | 147.35 | 92.87 | 1.426
2026-03-25 15:00 | 1774465200 | 1 | 0.0889 | 0.181 | 149.56 | 95.14 | 1.438
2026-03-25 16:00 | 1774468800 | 1 | 0.0778 | 0.156 | 152.22 | 86.65 | 1.495
2026-03-25 17:00 | 1774472400 | 1 | 0.0833 | 0.168 | 153.78 | 94.1 | 1.471
2026-03-25 18:00 | 1774476000 | 1 | 0.0944 | 0.189 | 155.04 | 100.84 | 1.499
2026-03-25 19:00 | 1774479600 | 1 | 0.0889 | 0.227 | 153.86 | 88.23 | 2.18
2026-03-25 20:00 | 1774483200 | 1 | 0.1722 | 0.416 | 145.1 | 90.14 | 3.353
2026-03-25 21:00 | 1774486800 | 1 | 0.1361 | 0.288 | 149.36 | 108.65 | 1.715
2026-03-25 22:00 | 1774490400 | 1 | 0.2167 | 0.528 | 159.32 | 104.98 | 4.204
2026-03-25 23:00 | 1774494000 | 1 | 0.2222 | 0.444 | 149.97 | 110.64 | 2.558
2026-03-26 00:00 | 1774497600 | 1 | 0.4194 | 0.874 | 141.58 | 108.45 | 4.244
2026-03-26 01:00 | 1774501200 | 1 | 0.2722 | 0.543 | 144.42 | 114.43 | 2.385
2026-03-26 02:00 | 1774504800 | 1 | 0.4278 | 0.869 | 142.4 | 109.81 | 4.152
2026-03-26 03:00 | 1774508400 | 1 | 0.3278 | 0.654 | 139.59 | 110.47 | 2.789
2026-03-26 04:00 | 1774512000 | 1 | 0.3778 | 0.721 | 151.3 | 112.85 | 4.063
2026-03-26 05:00 | 1774515600 | 1 | 0.2278 | 0.459 | 146.44 | 111.21 | 2.36
2026-03-26 06:00 | 1774519200 | 1 | 0.3083 | 0.592 | 143.45 | 106.95 | 3.16
2026-03-26 07:00 | 1774522800 | 1 | 0.3111 | 0.623 | 143.66 | 108.7 | 3.193
2026-03-26 08:00 | 1774526400 | 1 | 0.3444 | 0.648 | 142.39 | 108.04 | 3.261
2026-03-26 09:00 | 1774530000 | 1 | 0.2722 | 0.545 | 136.62 | 108.42 | 2.247
2026-03-26 10:00 | 1774533600 | 1 | 0.4 | 0.816 | 135.93 | 106.64 | 3.496
2026-03-26 11:00 | 1774537200 | 1 | 0.3278 | 0.659 | 134.04 | 107.02 | 2.603
2026-03-26 12:00 | 1774540800 | 1 | 0.1944 | 0.395 | 126.99 | 97 | 1.735
2026-03-26 13:00 | 1774544400 | 1 | 0.3556 | 0.744 | 111.89 | 95.77 | 1.756
2026-03-26 14:00 | 1774548000 | 1 | 0.4611 | 0.929 | 110.2 | 96.66 | 1.842
2026-03-26 15:00 | 1774551600 | 1 | 0.4056 | 0.889 | 125.51 | 99.1 | 3.442
2026-03-26 16:00 | 1774555200 | 1 | 0.1667 | 0.332 | 156.4 | 113.33 | 2.092
2026-03-26 17:00 | 1774558800 | 1 | 0.1444 | 0.258 | 150.12 | 95.68 | 2.06
2026-03-26 18:00 | 1774562400 | 1 | 0.1833 | 0.374 | 147.89 | 99.29 | 2.636
2026-03-26 19:00 | 1774566000 | 1 | 0 | 0 |  |  | 0
2026-03-26 20:00 | 1774569600 | 1 | 0.0611 | 0.092 | 138.39 | 75.27 | 0.851
2026-03-26 21:00 | 1774573200 | 1 | 0.1778 | 0.353 | 140.81 | 90.81 | 2.585
2026-03-26 22:00 | 1774576800 | 1 | 0.0944 | 0.19 | 138.53 | 96.91 | 1.154
2026-03-26 23:00 | 1774580400 | 1 | 0.2 | 0.402 | 136.86 | 98.8 | 2.231
2026-03-27 00:00 | 1774584000 | 1 | 0.2028 | 0.375 | 136.59 | 95.09 | 2.279
2026-03-27 01:00 | 1774587600 | 1 | 0.2722 | 0.545 | 130.88 | 101.82 | 2.322
2026-03-27 02:00 | 1774591200 | 1 | 0.2694 | 0.582 | 141.82 | 103.62 | 3.258
2026-03-27 03:00 | 1774594800 | 1 | 0.1444 | 0.288 | 138.61 | 100.43 | 1.611
2026-03-27 04:00 | 1774598400 | 1 | 0.3 | 0.565 | 136.31 | 100.36 | 2.968
2026-03-27 05:00 | 1774602000 | 1 | 0.2278 | 0.457 | 144.42 | 107.88 | 2.442
2026-03-27 06:00 | 1774605600 | 1 | 0.3417 | 0.643 | 141.11 | 105.23 | 3.379
2026-03-27 07:00 | 1774609200 | 1 | 0.1333 | 0.273 | 157.97 | 114.46 | 1.713
2026-03-27 08:00 | 1774612800 | 1 | 0.125 | 0.325 | 147.49 | 100.75 | 2.225
2026-03-27 09:00 | 1774616400 | 1 | 0.0861 | 0.172 | 136.58 | 88.22 | 1.216
2026-03-27 10:00 | 1774620000 | 1 | 0.2 | 0.388 | 137.98 | 89.8 | 2.736
2026-03-27 11:00 | 1774623600 | 1 | 0.1778 | 0.317 | 136.57 | 90.32 | 2.148
2026-03-27 12:00 | 1774627200 | 1 | 0 | 0 |  |  | 0
2026-03-27 13:00 | 1774630800 | 1 | 0.1528 | 0.272 | 136.14 | 84.28 | 2.062
2026-03-27 14:00 | 1774634400 | 1 | 0.1972 | 0.394 | 149.48 | 98.72 | 2.932
2026-03-27 15:00 | 1774638000 | 1 | 0.0944 | 0.188 | 147.67 | 100.45 | 1.3
2026-03-27 16:00 | 1774641600 | 1 | 0.1528 | 0.276 | 145.74 | 94.05 | 2.093
2026-03-27 17:00 | 1774645200 | 1 | 0.0917 | 0.184 | 141.3 | 90.89 | 1.358
2026-03-27 18:00 | 1774648800 | 1 | 0.2111 | 0.426 | 143.04 | 100.72 | 2.629
2026-03-27 19:00 | 1774652400 | 1 | 0.125 | 0.238 | 142.32 | 97.08 | 1.587
2026-03-27 20:00 | 1774656000 | 1 | 0.2778 | 0.523 | 150.24 | 98.85 | 3.936
2026-03-27 21:00 | 1774659600 | 1 | 0.225 | 0.447 | 149.95 | 111.13 | 2.54
2026-03-27 22:00 | 1774663200 | 1 | 0.3222 | 0.621 | 155.62 | 111.82 | 3.984
2026-03-27 23:00 | 1774666800 | 1 | 0.3389 | 0.674 | 156.41 | 115.87 | 4.007
2026-03-28 00:00 | 1774670400 | 1 | 0.3944 | 0.753 | 149.77 | 115.1 | 3.82
2026-03-28 01:00 | 1774674000 | 1 | 0.5139 | 1.049 | 146.37 | 115.57 | 4.733
2026-03-28 02:00 | 1774677600 | 1 | 0.5028 | 1.082 | 141.03 | 114.4 | 4.222
2026-03-28 03:00 | 1774681200 | 1 | 0.5111 | 1.037 | 146.49 | 121.75 | 3.755
2026-03-28 04:00 | 1774684800 | 1 | 0.5361 | 1.03 | 157.57 | 122.26 | 5.332
2026-03-28 05:00 | 1774688400 | 1 | 0.5417 | 1.04 | 148.56 | 117.59 | 4.716
2026-03-28 06:00 | 1774692000 | 1 | 0.5417 | 1.159 | 142.74 | 116.79 | 4.405
2026-03-28 07:00 | 1774695600 | 1 | 0.7333 | 1.506 | 132.52 | 116.58 | 3.517
2026-03-28 08:00 | 1774699200 | 1 | 0.4778 | 0.929 | 142.11 | 113.64 | 3.873
2026-03-28 09:00 | 1774702800 | 1 | 0.1917 | 0.384 | 148.92 | 103.89 | 2.515
2026-03-28 10:00 | 1774706400 | 1 | 0.2806 | 0.514 | 139.17 | 97.61 | 3.125
2026-03-28 11:00 | 1774710000 | 1 | 0.2222 | 0.402 | 142.06 | 102.24 | 2.347
2026-03-28 12:00 | 1774713600 | 1 | 0.1861 | 0.373 | 140.77 | 97.45 | 2.362
2026-03-28 13:00 | 1774717200 | 1 | 0.2778 | 0.512 | 139.76 | 98.44 | 3.097
2026-03-28 14:00 | 1774720800 | 1 | 0.0889 | 0.178 | 135.99 | 94.03 | 1.093
2026-03-28 15:00 | 1774724400 | 1 | 0.0889 | 0.179 | 134.42 | 90.19 | 1.162
2026-03-28 16:00 | 1774728000 | 1 | 0.2972 | 0.594 | 128.91 | 101.41 | 2.394
2026-03-28 17:00 | 1774731600 | 1 | 0.5 | 1.001 | 131.69 | 108.28 | 3.434
2026-03-28 18:00 | 1774735200 | 1 | 0.2944 | 0.588 | 134.71 | 110.77 | 2.062
2026-03-28 19:00 | 1774738800 | 1 | 0.4583 | 0.879 | 121.93 | 99.26 | 2.921
2026-03-28 20:00 | 1774742400 | 1 | 0.5667 | 1.131 | 134 | 111.3 | 3.761
2026-03-28 22:00 | 1774749600 | 1 | 0.8972 | 1.788 | 142.6 | 123.43 | 5.024
2026-03-28 23:00 | 1774753200 | 1 | 0.7778 | 1.641 | 139.59 | 120.13 | 4.68
2026-03-29 00:00 | 1774756800 | 1 | 0.7611 | 1.518 | 147.39 | 126.51 | 4.642
2026-03-29 01:00 | 1774760400 | 1 | 0.7278 | 1.543 | 146.89 | 122.73 | 5.46
2026-03-29 02:00 | 1774764000 | 1 | 0.8917 | 1.868 | 140.13 | 120.26 | 5.441
2026-03-29 03:00 | 1774767600 | 1 | 0.6139 | 1.217 | 153.7 | 129.79 | 4.264
2026-03-29 04:00 | 1774771200 | 1 | 0.75 | 1.588 | 141.04 | 119.62 | 4.979
2026-03-29 05:00 | 1774774800 | 1 | 0.8139 | 1.574 | 154.02 | 128.11 | 5.979
2026-03-29 06:00 | 1774778400 | 1 | 0.6833 | 1.357 | 142.08 | 122.55 | 3.881
2026-03-29 07:00 | 1774782000 | 1 | 0.6361 | 1.356 | 150.73 | 123.53 | 5.406
2026-03-29 08:00 | 1774785600 | 1 | 0.35 | 0.696 | 152.8 | 120.1 | 3.332
2026-03-29 09:00 | 1774789200 | 1 | 0.0972 | 0.194 | 145.9 | 100.14 | 1.303
2026-03-29 10:00 | 1774792800 | 1 | 0.2333 | 0.527 | 142.24 | 98.78 | 3.353
2026-03-29 11:00 | 1774796400 | 1 | 0.425 | 0.852 | 128.36 | 106.09 | 2.778
2026-03-29 12:00 | 1774800000 | 1 | 0.1556 | 0.313 | 139.55 | 100.37 | 1.791
2026-03-29 13:00 | 1774803600 | 1 | 0.1472 | 0.293 | 139.02 | 101.36 | 1.619
2026-03-29 14:00 | 1774807200 | 1 | 0.2222 | 0.45 | 136.54 | 102.69 | 2.233
2026-03-29 15:00 | 1774810800 | 1 | 0.35 | 0.694 | 132.23 | 105.05 | 2.762
2026-03-29 16:00 | 1774814400 | 0.95 | 0.3626 | 0.725 | 126.73 | 100.17 | 2.667
2026-03-29 17:00 | 1774818000 | 1 | 0.3111 | 0.619 | 133.47 | 106.73 | 2.424
2026-03-29 18:00 | 1774821600 | 1 | 0.4722 | 0.946 | 130.51 | 111.05 | 2.693
2026-03-29 19:00 | 1774825200 | 1 | 0.5722 | 1.145 | 129.7 | 110.22 | 3.268
2026-03-29 21:00 | 1774832400 | 1 | 0.3556 | 0.712 | 120.82 | 105.2 | 1.629
2026-03-29 22:00 | 1774836000 | 1 | 0.475 | 0.957 | 135.22 | 111.15 | 3.37
2026-03-29 23:00 | 1774839600 | 1 | 0.6694 | 1.339 | 137.26 | 118.35 | 3.709
2026-03-30 00:00 | 1774843200 | 1 | 0.75 | 1.589 | 138.02 | 117.54 | 4.768
2026-03-30 01:00 | 1774846800 | 1 | 0.5556 | 1.109 | 144.75 | 122.37 | 3.639
2026-03-30 02:00 | 1774850400 | 1 | 0.7389 | 1.572 | 131.01 | 113.33 | 4.071
2026-03-30 03:00 | 1774854000 | 1 | 0.5556 | 1.113 | 146.53 | 124.08 | 3.657
2026-03-30 04:00 | 1774857600 | 1 | 0.7278 | 1.517 | 126.88 | 112.14 | 3.273
2026-03-30 05:00 | 1774861200 | 1 | 0.8917 | 1.822 | 130.09 | 114.43 | 4.18
2026-03-30 06:00 | 1774864800 | 1 | 0.625 | 1.247 | 144.71 | 125.27 | 3.55
2026-03-30 07:00 | 1774868400 | 1 | 0.1972 | 0.353 | 132.61 | 105.68 | 1.392
2026-03-30 08:00 | 1774872000 | 1 | 0.0833 | 0.167 | 122.59 | 81.62 | 1
2026-03-30 09:00 | 1774875600 | 1 | 0.3056 | 0.569 | 123.52 | 93.64 | 2.488
2026-03-30 10:00 | 1774879200 | 1 | 0.4222 | 0.85 | 119.5 | 100.6 | 2.354
2026-03-30 11:00 | 1774882800 | 1 | 0.2861 | 0.592 | 141.04 | 105.56 | 3.079
2026-03-30 12:00 | 1774886400 | 1 | 0.0778 | 0.156 | 135.41 | 90.52 | 1.023
2026-03-30 14:00 | 1774893600 | 1 | 0.0778 | 0.156 | 131.14 | 78.86 | 1.191
2026-03-30 15:00 | 1774897200 | 1 | 0 | 0 |  |  | 0
2026-03-30 16:00 | 1774900800 | 1 | 0.0833 | 0.169 | 126.37 | 79.86 | 1.149
2026-03-30 17:00 | 1774904400 | 1 | 0.1944 | 0.39 | 130.63 | 92.18 | 2.193
2026-03-30 18:00 | 1774908000 | 1 | 0.0944 | 0.189 | 130.89 | 93.63 | 1.032
2026-03-30 19:00 | 1774911600 | 1 | 0.0972 | 0.195 | 129.6 | 92.89 | 1.049
2026-03-30 20:00 | 1774915200 | 1 | 0.1694 | 0.338 | 129.13 | 91.31 | 1.875
2026-03-30 21:00 | 1774918800 | 1 | 0.1028 | 0.197 | 129.11 | 94.89 | 0.986
2026-03-30 22:00 | 1774922400 | 1 | 0.1944 | 0.391 | 121.5 | 91.98 | 1.689
2026-03-30 23:00 | 1774926000 | 1 | 0.1889 | 0.378 | 132.54 | 96.53 | 1.997
2026-03-31 00:00 | 1774929600 | 1 | 0.0944 | 0.189 | 135.2 | 95.59 | 1.098
2026-03-31 01:00 | 1774933200 | 1 | 0.2056 | 0.412 | 148.44 | 98 | 3.041
2026-03-31 02:00 | 1774936800 | 1 | 0.175 | 0.305 | 147.26 | 96.21 | 2.278
2026-03-31 03:00 | 1774940400 | 1 | 0.1972 | 0.389 | 146.39 | 102.07 | 2.527
2026-03-31 04:00 | 1774944000 | 1 | 0.0944 | 0.191 | 140.97 | 100.26 | 1.134
2026-03-31 05:00 | 1774947600 | 1 | 0.3278 | 0.753 | 129.13 | 97.33 | 3.511
2026-03-31 06:00 | 1774951200 | 1 | 0.2194 | 0.44 | 137.97 | 106.07 | 2.049
2026-03-31 07:00 | 1774954800 | 1 | 0.3 | 0.562 | 135.03 | 101.57 | 2.752
2026-03-31 08:00 | 1774958400 | 1 | 0.2222 | 0.447 | 133.43 | 103.75 | 1.943
2026-03-31 09:00 | 1774962000 | 1 | 0.2944 | 0.587 | 131.85 | 100.84 | 2.669
2026-03-31 10:00 | 1774965600 | 1 | 0.3611 | 0.723 | 131.53 | 104.79 | 2.833
2026-03-31 11:00 | 1774969200 | 1 | 0.2972 | 0.599 | 126.54 | 104.46 | 1.931
2026-03-31 12:00 | 1774972800 | 1 | 0.3694 | 0.837 | 118.5 | 99.8 | 2.293
2026-03-31 13:00 | 1774976400 | 1 | 0.4472 | 0.853 | 130.89 | 102.98 | 3.489
2026-03-31 14:00 | 1774980000 | 1 | 0.2528 | 0.505 | 135.6 | 108.44 | 2.009
2026-03-31 15:00 | 1774983600 | 1 | 0.325 | 0.742 | 128.52 | 99.39 | 3.16
2026-03-31 16:00 | 1774987200 | 1 | 0.275 | 0.549 | 129.68 | 105.21 | 1.969
2026-03-31 17:00 | 1774990800 | 1 | 0.1278 | 0.311 | 131.53 | 94.42 | 1.692
2026-03-31 19:00 | 1774998000 | 1 | 0.3944 | 0.886 | 120.15 | 98.93 | 2.755
2026-03-31 20:00 | 1775001600 | 0.9528 | 0.6064 | 1.22 | 114.46 | 97.58 | 2.874
2026-03-31 21:00 | 1775005200 | 1 | 0.7222 | 1.546 | 124.55 | 107.2 | 3.926
2026-03-31 22:00 | 1775008800 | 1 | 0.6472 | 1.297 | 132.72 | 115.25 | 3.322
2026-03-31 23:00 | 1775012400 | 1 | 0.675 | 1.36 | 128.58 | 113.43 | 3.016
2026-04-01 00:00 | 1775016000 | 0.9972 | 0.7382 | 1.568 | 124.82 | 109.97 | 3.402
2026-04-01 01:00 | 1775019600 | 1 | 0.7333 | 1.562 | 127.19 | 110.24 | 3.879
2026-04-01 02:00 | 1775023200 | 1 | 0.7444 | 1.497 | 125.53 | 110.03 | 3.403
2026-04-01 03:00 | 1775026800 | 1 | 0.5306 | 1.067 | 133.81 | 117.35 | 2.568
2026-04-01 04:00 | 1775030400 | 0.95 | 0.6608 | 1.608 | 129.32 | 106.61 | 5.084
2026-04-01 05:00 | 1775034000 | 1 | 0.6194 | 1.245 | 128.19 | 110.02 | 3.311
2026-04-01 06:00 | 1775037600 | 1 | 0.3139 | 0.624 | 147.6 | 119.97 | 2.526
2026-04-01 07:00 | 1775041200 | 1 | 0.3278 | 0.694 | 140.46 | 105.07 | 3.589
2026-04-01 08:00 | 1775044800 | 1 | 0.2972 | 0.595 | 132.6 | 106.47 | 2.278
2026-04-01 09:00 | 1775048400 | 1 | 0.3861 | 0.772 | 129.87 | 107.34 | 2.55
2026-04-01 10:00 | 1775052000 | 1 | 0.4278 | 0.86 | 128.6 | 105.69 | 2.881
2026-04-01 11:00 | 1775055600 | 1 | 0.425 | 0.849 | 127.96 | 107.96 | 2.488
2026-04-01 12:00 | 1775059200 | 1 | 0.3472 | 0.79 | 120.43 | 95.12 | 2.928
2026-04-01 13:00 | 1775062800 | 1 | 0.2194 | 0.436 | 131.12 | 101.97 | 1.864
2026-04-01 14:00 | 1775066400 | 1 | 0.1694 | 0.342 | 130.66 | 95.5 | 1.75
2026-04-01 15:00 | 1775070000 | 1 | 0.1444 | 0.288 | 136.44 | 102.98 | 1.412
2026-04-01 16:00 | 1775073600 | 1 | 0.2389 | 0.477 | 138.53 | 102.99 | 2.482
2026-04-01 17:00 | 1775077200 | 1 | 0.2972 | 0.596 | 137.33 | 108.48 | 2.514
2026-04-01 18:00 | 1775080800 | 1 | 0.2444 | 0.489 | 134.1 | 107.08 | 1.936
2026-04-01 19:00 | 1775084400 | 1 | 0.3833 | 0.768 | 132.1 | 107.7 | 2.745
2026-04-01 20:00 | 1775088000 | 1 | 0.4194 | 0.841 | 125.88 | 107.04 | 2.323
2026-04-01 21:00 | 1775091600 | 1 | 0.5111 | 1.008 | 130.11 | 106.37 | 3.505
2026-04-01 22:00 | 1775095200 | 1 | 0.4389 | 0.878 | 130.6 | 111.57 | 2.448
2026-04-01 23:00 | 1775098800 | 1 | 0.6028 | 1.175 | 131.72 | 109.21 | 3.875
2026-04-02 00:00 | 1775102400 | 1 | 0.4278 | 0.857 | 138.06 | 113.42 | 3.091
2026-04-02 01:00 | 1775106000 | 1 | 0.2972 | 0.612 | 138.79 | 110.93 | 2.499
2026-04-02 02:00 | 1775109600 | 1 | 0.3861 | 0.848 | 139.37 | 109.87 | 3.667
2026-04-02 03:00 | 1775113200 | 1 | 0.4056 | 0.81 | 139.71 | 113.3 | 3.134
2026-04-02 04:00 | 1775116800 | 1 | 0.4 | 0.785 | 135.63 | 109.15 | 3.046
2026-04-02 05:00 | 1775120400 | 1 | 0.5778 | 1.215 | 128.92 | 109.7 | 3.417
2026-04-02 06:00 | 1775124000 | 1 | 0.7056 | 1.418 | 131.88 | 113.67 | 3.783
2026-04-02 07:00 | 1775127600 | 1 | 0.4611 | 0.948 | 142.61 | 113.38 | 4.06
2026-04-02 08:00 | 1775131200 | 1 | 0.3694 | 0.745 | 138.73 | 115.97 | 2.48
2026-04-02 09:00 | 1775134800 | 1 | 0.5722 | 1.144 | 127.39 | 105.58 | 3.656
2026-04-02 10:00 | 1775138400 | 1 | 0.3778 | 0.755 | 136.79 | 110.41 | 2.917
2026-04-02 11:00 | 1775142000 | 1 | 0.175 | 0.348 | 133.19 | 98.85 | 1.753
2026-04-02 12:00 | 1775145600 | 1 | 0.1028 | 0.215 | 130.83 | 94.86 | 1.109
2026-04-02 13:00 | 1775149200 | 1 | 0.0833 | 0.166 | 132.41 | 90.4 | 1.02
2026-04-02 14:00 | 1775152800 | 1 | 0.0833 | 0.166 | 124.88 | 85.53 | 0.958
2026-04-02 15:00 | 1775156400 | 1 | 0.0833 | 0.166 | 133.21 | 88.12 | 1.1
2026-04-02 16:00 | 1775160000 | 1 | 0 | 0 |  |  | 0
2026-04-02 17:00 | 1775163600 | 1 | 0.0778 | 0.158 | 124.43 | 77.08 | 1.096
2026-04-02 18:00 | 1775167200 | 1 | 0 | 0 |  |  | 0
2026-04-02 19:00 | 1775170800 | 1 | 0.1667 | 0.333 | 138.47 | 87.97 | 2.461
2026-04-02 20:00 | 1775174400 | 1 | 0.1083 | 0.218 | 142.37 | 98.6 | 1.397
2026-04-02 21:00 | 1775178000 | 1 | 0.1444 | 0.288 | 142.39 | 93.23 | 2.075
2026-04-02 22:00 | 1775181600 | 1 | 0.1028 | 0.207 | 139.42 | 97.12 | 1.281
2026-04-02 23:00 | 1775185200 | 1 | 0.2861 | 0.577 | 129.87 | 100.55 | 2.478
2026-04-03 00:00 | 1775188800 | 1 | 0.325 | 0.65 | 144.8 | 113.36 | 2.994
2026-04-03 01:00 | 1775192400 | 1 | 0.2556 | 0.517 | 137.78 | 110.39 | 2.066
2026-04-03 02:00 | 1775196000 | 1 | 0.4417 | 0.94 | 133.62 | 106.41 | 3.749
2026-04-03 03:00 | 1775199600 | 1 | 0.4667 | 0.936 | 131.66 | 109.8 | 2.999
2026-04-03 04:00 | 1775203200 | 1 | 0.4417 | 0.948 | 136.42 | 109.46 | 3.736
2026-04-03 05:00 | 1775206800 | 1 | 0.3528 | 0.706 | 140.36 | 115.87 | 2.535
2026-04-03 06:00 | 1775210400 | 1 | 0.4167 | 0.84 | 130.23 | 109.72 | 2.523
2026-04-03 07:00 | 1775214000 | 1 | 0.4389 | 0.976 | 143.4 | 110.97 | 4.637
2026-04-03 08:00 | 1775217600 | 1 | 0.25 | 0.5 | 142.62 | 112.59 | 2.198
2026-04-03 09:00 | 1775221200 | 1 | 0.4278 | 0.921 | 139.57 | 109.76 | 4.025
2026-04-03 10:00 | 1775224800 | 1 | 0.4306 | 0.861 | 135.39 | 112.65 | 2.87
2026-04-03 11:00 | 1775228400 | 0.95 | 0.5702 | 1.142 | 130.78 | 108.07 | 3.609
2026-04-03 12:00 | 1775232000 | 1 | 0.5583 | 1.096 | 134.44 | 114.24 | 3.245
2026-04-03 13:00 | 1775235600 | 1 | 0.4389 | 0.881 | 143.59 | 115.09 | 3.68
2026-04-03 14:00 | 1775239200 | 1 | 0.1639 | 0.292 | 147.47 | 98.57 | 2.092
2026-04-03 15:00 | 1775242800 | 1 | 0.1778 | 0.358 | 143.61 | 97.97 | 2.393
2026-04-03 16:00 | 1775246400 | 1 | 0.1028 | 0.206 | 162.27 | 104.83 | 1.73
2026-04-03 17:00 | 1775250000 | 1 | 0.1444 | 0.295 | 164.37 | 100.88 | 2.742
2026-04-03 18:00 | 1775253600 | 1 | 0.2 | 0.399 | 154.34 | 106.92 | 2.773
2026-04-03 19:00 | 1775257200 | 1 | 0.2056 | 0.418 | 146.08 | 107.07 | 2.374
2026-04-03 20:00 | 1775260800 | 1 | 0.2444 | 0.532 | 154.95 | 104.68 | 3.916
2026-04-03 21:00 | 1775264400 | 1 | 0.1 | 0.204 | 155.23 | 108.69 | 1.381
2026-04-03 22:00 | 1775268000 | 1 | 0.2167 | 0.434 | 148.12 | 107.94 | 2.558
2026-04-03 23:00 | 1775271600 | 1 | 0.2444 | 0.529 | 144.84 | 102.19 | 3.309
2026-04-04 00:00 | 1775275200 | 1 | 0.2361 | 0.472 | 141.32 | 109.5 | 2.201
2026-04-04 01:00 | 1775278800 | 1 | 0.3694 | 0.744 | 139.46 | 109.92 | 3.214
2026-04-04 02:00 | 1775282400 | 1 | 0.1778 | 0.32 | 143.46 | 101.91 | 1.951
2026-04-04 03:00 | 1775286000 | 1 | 0.0833 | 0.167 | 145.71 | 94.48 | 1.251
2026-04-04 04:00 | 1775289600 | 1 | 0.1944 | 0.395 | 142.33 | 98.94 | 2.496
2026-04-04 05:00 | 1775293200 | 1 | 0.2444 | 0.451 | 143.22 | 97.06 | 3.051
2026-04-04 06:00 | 1775296800 | 1 | 0.1306 | 0.26 | 142.21 | 106.6 | 1.354
2026-04-04 07:00 | 1775300400 | 1 | 0.3556 | 0.685 | 132.05 | 99.57 | 3.262
2026-04-04 08:00 | 1775304000 | 1 | 0.1694 | 0.34 | 134.12 | 104.91 | 1.455
2026-04-04 09:00 | 1775307600 | 1 | 0.7833 | 1.654 | 139.28 | 116.57 | 5.502
2026-04-04 10:00 | 1775311200 | 1 | 0.3056 | 0.612 | 134.52 | 111 | 2.111
2026-04-04 11:00 | 1775314800 | 1 | 0.1722 | 0.306 | 134.62 | 95.57 | 1.751
2026-04-04 12:00 | 1775318400 | 1 | 0.0972 | 0.193 | 140.87 | 90.87 | 1.413
2026-04-04 13:00 | 1775322000 | 1 | 0 | 0 |  |  | 0
2026-04-04 14:00 | 1775325600 | 1 | 0 | 0 |  |  | 0
2026-04-04 15:00 | 1775329200 | 1 | 0.0806 | 0.161 | 139.12 | 79.11 | 1.414
2026-04-04 16:00 | 1775332800 | 1 | 0.0917 | 0.182 | 138.88 | 87.57 | 1.369
2026-04-04 17:00 | 1775336400 | 1 | 0.0917 | 0.187 | 144.78 | 94.95 | 1.359
2026-04-04 18:00 | 1775340000 | 1 | 0.0917 | 0.182 | 145.4 | 95.46 | 1.33
2026-04-04 19:00 | 1775343600 | 1 | 0 | 0 |  |  | 0
2026-04-04 20:00 | 1775347200 | 1 | 0.0833 | 0.167 | 136.14 | 80.09 | 1.368
2026-04-04 21:00 | 1775350800 | 1 | 0.1083 | 0.219 | 144.23 | 99.16 | 1.433
2026-04-04 22:00 | 1775354400 | 1 | 0.2056 | 0.414 | 136.88 | 99.45 | 2.267
2026-04-04 23:00 | 1775358000 | 1 | 0.225 | 0.527 | 147 | 99.37 | 3.678
2026-04-05 00:00 | 1775361600 | 1 | 0.1722 | 0.349 | 146.5 | 102.54 | 2.248
2026-04-05 01:00 | 1775365200 | 1 | 0.2361 | 0.47 | 137.81 | 105.92 | 2.196
2026-04-05 02:00 | 1775368800 | 1 | 0.35 | 0.664 | 135.67 | 104.45 | 3.036
2026-04-05 03:00 | 1775372400 | 1 | 0.2944 | 0.546 | 147.91 | 106.39 | 3.324
2026-04-05 04:00 | 1775376000 | 1 | 0.225 | 0.448 | 143.45 | 108.41 | 2.297
2026-04-05 05:00 | 1775379600 | 1 | 0.3278 | 0.614 | 132.02 | 102.75 | 2.632
2026-04-05 06:00 | 1775383200 | 1 | 0.3667 | 0.729 | 137.93 | 108.47 | 3.148
2026-04-05 07:00 | 1775386800 | 1 | 0.3111 | 0.583 | 145.09 | 106.46 | 3.296
2026-04-05 08:00 | 1775390400 | 1 | 0.2083 | 0.414 | 144.44 | 106 | 2.327
2026-04-05 09:00 | 1775394000 | 1 | 0.2972 | 0.563 | 141.36 | 101.53 | 3.269
2026-04-05 10:00 | 1775397600 | 1 | 0.65 | 1.297 | 131.95 | 114.42 | 3.33
2026-04-05 11:00 | 1775401200 | 1 | 0.4833 | 1.063 | 129.08 | 106.55 | 3.5
2026-04-05 12:00 | 1775404800 | 1 | 0.3139 | 0.629 | 139.19 | 114.08 | 2.309
2026-04-05 13:00 | 1775408400 | 1 | 0.3694 | 0.723 | 126.04 | 100.08 | 2.75
2026-04-05 14:00 | 1775412000 | 1 | 0.1889 | 0.383 | 146.07 | 108.45 | 2.11
2026-04-05 15:00 | 1775415600 | 1 | 0.3778 | 0.751 | 131.11 | 99.91 | 3.398
2026-04-05 16:00 | 1775419200 | 1 | 0.2306 | 0.452 | 153.54 | 109.61 | 2.906
2026-04-05 17:00 | 1775422800 | 1 | 0.1667 | 0.334 | 139.17 | 100.75 | 1.88
2026-04-05 18:00 | 1775426400 | 1 | 0.2806 | 0.564 | 135.92 | 106.24 | 2.444
2026-04-05 19:00 | 1775430000 | 1 | 0.2333 | 0.519 | 145.49 | 102.45 | 3.275
2026-04-05 20:00 | 1775433600 | 1 | 0.2111 | 0.423 | 139.63 | 104.47 | 2.179
2026-04-05 21:00 | 1775437200 | 1 | 0.225 | 0.446 | 134.45 | 104.58 | 1.95
2026-04-05 22:00 | 1775440800 | 1 | 0.2611 | 0.579 | 134.26 | 101.9 | 2.743
2026-04-05 23:00 | 1775444400 | 1 | 0.2972 | 0.592 | 129.96 | 103.93 | 2.257
2026-04-06 00:00 | 1775448000 | 1 | 0.3139 | 0.634 | 132.43 | 107.22 | 2.341
2026-04-06 01:00 | 1775451600 | 1 | 0.2861 | 0.669 | 131 | 100.64 | 2.97
2026-04-06 02:00 | 1775455200 | 1 | 0.3361 | 0.674 | 135.82 | 109.83 | 2.567
2026-04-06 03:00 | 1775458800 | 1 | 0.3167 | 0.596 | 133.55 | 103.7 | 2.606
2026-04-06 04:00 | 1775462400 | 1 | 0.3028 | 0.643 | 141.97 | 105.15 | 3.472
2026-04-06 05:00 | 1775466000 | 1 | 0.1417 | 0.32 | 140.77 | 100.14 | 1.905
2026-04-06 06:00 | 1775469600 | 1 | 0.0944 | 0.187 | 147.93 | 100.38 | 1.306
2026-04-06 07:00 | 1775473200 | 1 | 0.1694 | 0.298 | 148.04 | 96.07 | 2.267
2026-04-06 08:00 | 1775476800 | 1 | 0.0861 | 0.171 | 141.87 | 89.01 | 1.328
2026-04-06 09:00 | 1775480400 | 1 | 0.0861 | 0.172 | 140.84 | 87.93 | 1.334
2026-04-06 10:00 | 1775484000 | 1 | 0.1667 | 0.297 | 144.72 | 92.42 | 2.271
2026-04-06 11:00 | 1775487600 | 1 | 0.0917 | 0.183 | 137.85 | 93.56 | 1.186
2026-04-06 12:00 | 1775491200 | 1 | 0.0917 | 0.183 | 118.23 | 83.31 | 0.939
2026-04-06 13:00 | 1775494800 | 1 | 0.0917 | 0.185 | 138.8 | 89.26 | 1.33
2026-04-06 14:00 | 1775498400 | 1 | 0.1583 | 0.289 | 146.99 | 90.76 | 2.38
2026-04-06 15:00 | 1775502000 | 1 | 0.0917 | 0.183 | 143.17 | 94.09 | 1.317
2026-04-06 16:00 | 1775505600 | 1 | 0.1 | 0.202 | 145.65 | 97.41 | 1.42
2026-04-06 17:00 | 1775509200 | 1 | 0.2472 | 0.464 | 151.49 | 97.41 | 3.671
2026-04-06 18:00 | 1775512800 | 1 | 0.0889 | 0.177 | 148.59 | 99.85 | 1.263
2026-04-06 19:00 | 1775516400 | 1 | 0.0778 | 0.156 | 142.93 | 87.71 | 1.259
2026-04-06 20:00 | 1775520000 | 1 | 0.2694 | 0.492 | 144.82 | 94.97 | 3.592
2026-04-06 21:00 | 1775523600 | 1 | 0.1528 | 0.305 | 144.65 | 107.71 | 1.653
2026-04-06 22:00 | 1775527200 | 1 | 0.3778 | 0.713 | 144.15 | 104.72 | 4.119
2026-04-06 23:00 | 1775530800 | 1 | 0.2667 | 0.532 | 139.74 | 111.15 | 2.228
2026-04-07 00:00 | 1775534400 | 1 | 0.2806 | 0.641 | 142.34 | 107.13 | 3.303
2026-04-07 01:00 | 1775538000 | 0.9833 | 0.452 | 0.9 | 139.2 | 106.17 | 4.279
2026-04-07 02:00 | 1775541600 | 0.9667 | 0.3103 | 0.724 | 136.8 | 105.79 | 3.18
2026-04-07 03:00 | 1775545200 | 1 | 0.4083 | 0.855 | 146.74 | 110.12 | 4.577
2026-04-07 04:00 | 1775548800 | 1 | 0.2389 | 0.477 | 143.52 | 111.16 | 2.262
2026-04-07 05:00 | 1775552400 | 1 | 0.3111 | 0.585 | 152.39 | 109.06 | 3.711
2026-04-07 06:00 | 1775556000 | 1 | 0.3 | 0.6 | 144.59 | 110.47 | 3
2026-04-07 07:00 | 1775559600 | 1 | 0.2444 | 0.451 | 153.65 | 108.18 | 3.001
2026-04-07 08:00 | 1775563200 | 1 | 0.0833 | 0.17 | 147.54 | 93.45 | 1.344
2026-04-07 09:00 | 1775566800 | 1 | 0.0806 | 0.164 | 142.28 | 86.11 | 1.335
2026-04-07 10:00 | 1775570400 | 1 | 0.0333 | 0.048 | 142.42 | 72.84 | 0.493
2026-04-07 11:00 | 1775574000 | 1 | 0.0778 | 0.155 | 142.72 | 84.67 | 1.318
2026-04-07 12:00 | 1775577600 | 1 | 0.0889 | 0.178 | 141.18 | 89.48 | 1.345
2026-04-07 13:00 | 1775581200 | 1 | 0.1833 | 0.366 | 133.48 | 91.65 | 2.245
2026-04-07 14:00 | 1775584800 | 1 | 0.0917 | 0.182 | 138.04 | 93.28 | 1.197
2026-04-07 15:00 | 1775588400 | 1 | 0.0917 | 0.187 | 146.7 | 97.52 | 1.335
2026-04-07 16:00 | 1775592000 | 1 | 0.1833 | 0.365 | 148.21 | 98.74 | 2.645
2026-04-07 17:00 | 1775595600 | 1 | 0.0917 | 0.184 | 147.01 | 99.68 | 1.275
2026-04-07 18:00 | 1775599200 | 1 | 0.2 | 0.401 | 142.54 | 100.3 | 2.48
2026-04-07 19:00 | 1775602800 | 1 | 0.2361 | 0.472 | 138.57 | 111.26 | 1.889
2026-04-07 20:00 | 1775606400 | 1 | 0.3 | 0.597 | 137.45 | 104.96 | 2.842
2026-04-07 21:00 | 1775610000 | 1 | 0.2889 | 0.574 | 135.51 | 108.49 | 2.27
2026-04-07 22:00 | 1775613600 | 1 | 0.3806 | 0.76 | 146.84 | 114.1 | 3.646
2026-04-07 23:00 | 1775617200 | 1 | 0.35 | 0.782 | 140.93 | 111.54 | 3.365
2026-04-08 00:00 | 1775620800 | 0.9944 | 0.3464 | 0.689 | 148.29 | 115.08 | 3.329
2026-04-08 01:00 | 1775624400 | 1 | 0.3556 | 0.794 | 147.66 | 114.54 | 3.844
2026-04-08 02:00 | 1775628000 | 1 | 0.4056 | 0.803 | 149.75 | 118.64 | 3.663
2026-04-08 03:00 | 1775631600 | 1 | 0.35 | 0.779 | 145.35 | 111.42 | 3.872
2026-04-08 04:00 | 1775635200 | 0.9556 | 0.5959 | 1.191 | 137.73 | 118.76 | 3.163
2026-04-08 05:00 | 1775638800 | 1 | 0.6056 | 1.294 | 144.03 | 117.25 | 5.077
2026-04-08 06:00 | 1775642400 | 1 | 0.4361 | 0.87 | 155.23 | 123.65 | 4.024
2026-04-08 07:00 | 1775646000 | 1 | 0.2611 | 0.6 | 149.92 | 110.35 | 3.476
2026-04-08 08:00 | 1775649600 | 1 | 0.1222 | 0.242 | 144.05 | 102.27 | 1.484
2026-04-08 09:00 | 1775653200 | 1 | 0.1694 | 0.34 | 145.44 | 99.5 | 2.286
2026-04-08 10:00 | 1775656800 | 1 | 0.0972 | 0.193 | 143 | 98.35 | 1.266
2026-04-08 11:00 | 1775660400 | 1 | 0.1556 | 0.308 | 141.9 | 92.21 | 2.243
2026-04-08 12:00 | 1775664000 | 1 | 0.025 | 0.051 | 147.14 | 110.28 | 0.275
2026-04-08 13:00 | 1775667600 | 1 | 0.0861 | 0.172 | 147.8 | 88.66 | 1.493
2026-04-08 14:00 | 1775671200 | 1 | 0.1833 | 0.368 | 140.29 | 94.64 | 2.463
2026-04-08 15:00 | 1775674800 | 1 | 0.0917 | 0.181 | 149.78 | 99.85 | 1.325
2026-04-08 16:00 | 1775678400 | 1 | 0.0917 | 0.183 | 144 | 93.81 | 1.335
2026-04-08 17:00 | 1775682000 | 1 | 0.125 | 0.249 | 145.84 | 93.17 | 1.923
2026-04-08 18:00 | 1775685600 | 1 | 0.1528 | 0.307 | 148.12 | 103.98 | 1.985
2026-04-08 19:00 | 1775689200 | 1 | 0.2056 | 0.413 | 146.66 | 103.91 | 2.57
2026-04-08 20:00 | 1775692800 | 1 | 0.1556 | 0.311 | 143.93 | 99.7 | 2.006
2026-04-08 21:00 | 1775696400 | 1 | 0.0306 | 0.062 | 148.1 | 111.47 | 0.333
2026-04-08 22:00 | 1775700000 | 1 | 0.0889 | 0.178 | 143.34 | 89.15 | 1.408
2026-04-08 23:00 | 1775703600 | 1 | 0.2194 | 0.439 | 136.05 | 99.75 | 2.332
2026-04-09 00:00 | 1775707200 | 1 | 0.2694 | 0.517 | 155.23 | 106.17 | 3.709
2026-04-09 01:00 | 1775710800 | 1 | 0.2222 | 0.444 | 155.82 | 111.75 | 2.861
2026-04-09 02:00 | 1775714400 | 1 | 0.2972 | 0.564 | 152.36 | 108.43 | 3.613
2026-04-09 03:00 | 1775718000 | 1 | 0.35 | 0.699 | 145.84 | 111.7 | 3.495
2026-04-09 04:00 | 1775721600 | 1 | 0.2833 | 0.569 | 142.59 | 113.24 | 2.445
2026-04-09 05:00 | 1775725200 | 1 | 0.45 | 0.893 | 143.93 | 111.34 | 4.261
2026-04-09 06:00 | 1775728800 | 1 | 0.2667 | 0.534 | 142.48 | 113.24 | 2.289
2026-04-09 07:00 | 1775732400 | 1 | 0.2639 | 0.521 | 139.5 | 109.51 | 2.286
2026-04-09 08:00 | 1775736000 | 1 | 0.2306 | 0.457 | 138.53 | 96.64 | 2.794
2026-04-09 09:00 | 1775739600 | 1 | 0.0889 | 0.178 | 132.78 | 92.3 | 1.056
2026-04-09 10:00 | 1775743200 | 1 | 0.0917 | 0.184 | 130.5 | 90.96 | 1.064
2026-04-09 11:00 | 1775746800 | 1 | 0.0333 | 0.067 | 121.01 | 73.09 | 0.47
2026-04-09 12:00 | 1775750400 | 1 | 0.0472 | 0.096 | 129.6 | 87.51 | 0.58
2026-04-09 13:00 | 1775754000 | 1 | 0.0833 | 0.167 | 140.91 | 85.36 | 1.36
2026-04-09 14:00 | 1775757600 | 1 | 0 | 0 |  |  | 0
2026-04-09 15:00 | 1775761200 | 1 | 0.0778 | 0.156 | 135.68 | 84.27 | 1.173
2026-04-09 16:00 | 1775764800 | 1 | 0.0889 | 0.178 | 148.41 | 90.38 | 1.514
2026-04-09 17:00 | 1775768400 | 1 | 0.0917 | 0.181 | 149.4 | 95 | 1.444
2026-04-09 18:00 | 1775772000 | 1 | 0.0889 | 0.178 | 149.96 | 94.93 | 1.433
2026-04-09 19:00 | 1775775600 | 1 | 0.1889 | 0.379 | 148.98 | 99.43 | 2.748
2026-04-09 20:00 | 1775779200 | 1 | 0 | 0 |  |  | 0
2026-04-09 21:00 | 1775782800 | 1 | 0 | 0 |  |  | 0
2026-04-09 22:00 | 1775786400 | 1 | 0.0861 | 0.176 | 147.47 | 83.25 | 1.648
2026-04-09 23:00 | 1775790000 | 1 | 0.0889 | 0.178 | 146.5 | 95.81 | 1.323
2026-04-10 00:00 | 1775793600 | 1 | 0.1944 | 0.394 | 154.57 | 103.69 | 2.935
2026-04-10 01:00 | 1775797200 | 1 | 0.25 | 0.473 | 157.96 | 102.84 | 3.815
2026-04-10 02:00 | 1775800800 | 1 | 0.1 | 0.2 | 154.02 | 106.42 | 1.396
2026-04-10 03:00 | 1775804400 | 1 | 0.0694 | 0.14 | 146.55 | 86.19 | 1.235
2026-04-10 04:00 | 1775808000 | 1 | 0.1861 | 0.351 | 149.39 | 98.89 | 2.599
2026-04-10 05:00 | 1775811600 | 1 | 0.1083 | 0.217 | 147.12 | 102.22 | 1.425
2026-04-10 06:00 | 1775815200 | 1 | 0.1889 | 0.377 | 153.13 | 103.88 | 2.713
2026-04-10 07:00 | 1775818800 | 1 | 0.1417 | 0.258 | 145.12 | 95.47 | 1.881
2026-04-10 08:00 | 1775822400 | 1 | 0.0861 | 0.171 | 140.21 | 86.95 | 1.335
2026-04-10 09:00 | 1775826000 | 1 | 0 | 0 |  |  | 0
2026-04-10 10:00 | 1775829600 | 1 | 0.075 | 0.149 | 137.27 | 79.48 | 1.265
2026-04-10 11:00 | 1775833200 | 1 | 0 | 0 |  |  | 0
2026-04-10 12:00 | 1775836800 | 1 | 0 | 0 |  |  | 0
2026-04-10 13:00 | 1775840400 | 1 | 0 | 0 |  |  | 0
2026-04-10 14:00 | 1775844000 | 1 | 0.0861 | 0.176 | 161.81 | 86.21 | 1.931
2026-04-10 15:00 | 1775847600 | 1 | 0 | 0 |  |  | 0
2026-04-10 16:00 | 1775851200 | 1 | 0 | 0 |  |  | 0
2026-04-10 17:00 | 1775854800 | 1 | 0.0972 | 0.196 | 159.97 | 91.83 | 1.959
2026-04-10 18:00 | 1775858400 | 1 | 0.0806 | 0.163 | 155.6 | 89.18 | 1.572
2026-04-10 19:00 | 1775862000 | 1 | 0 | 0 |  |  | 0
2026-04-10 20:00 | 1775865600 | 1 | 0 | 0 |  |  | 0
2026-04-10 21:00 | 1775869200 | 1 | 0 | 0 |  |  | 0
2026-04-10 22:00 | 1775872800 | 1 | 0 | 0 |  |  | 0
2026-04-10 23:00 | 1775876400 | 1 | 0.1278 | 0.256 | 138.86 | 83.74 | 2.067
2026-04-11 00:00 | 1775880000 | 1 | 0.0917 | 0.186 | 142.68 | 94.11 | 1.325
2026-04-11 01:00 | 1775883600 | 1 | 0.0917 | 0.183 | 134.48 | 93.81 | 1.093
2026-04-11 02:00 | 1775887200 | 1 | 0.0972 | 0.193 | 136.03 | 95.96 | 1.135
2026-04-11 03:00 | 1775890800 | 1 | 0.2056 | 0.415 | 123.7 | 94.48 | 1.768
2026-04-11 04:00 | 1775894400 | 1 | 0.2417 | 0.476 | 142.16 | 96.45 | 3.187
2026-04-11 05:00 | 1775898000 | 1 | 0.0972 | 0.191 | 152.01 | 100.54 | 1.442
2026-04-11 06:00 | 1775901600 | 1 | 0.0972 | 0.197 | 146.5 | 99.5 | 1.348
2026-04-11 07:00 | 1775905200 | 1 | 0.0861 | 0.175 | 144.09 | 95.1 | 1.247
2026-04-11 08:00 | 1775908800 | 1 | 0 | 0 |  |  | 0
2026-04-11 09:00 | 1775912400 | 1 | 0.0861 | 0.175 | 135.96 | 82.55 | 1.368
2026-04-11 10:00 | 1775916000 | 1 | 0 | 0 |  |  | 0
2026-04-11 11:00 | 1775919600 | 1 | 0.1778 | 0.353 | 138.78 | 91.34 | 2.457
2026-04-11 12:00 | 1775923200 | 1 | 0.0917 | 0.188 | 137.51 | 92.16 | 1.236
2026-04-11 13:00 | 1775926800 | 1 | 0 | 0 |  |  | 0
2026-04-11 14:00 | 1775930400 | 1 | 0.0806 | 0.163 | 147.64 | 87.52 | 1.425
2026-04-11 15:00 | 1775934000 | 1 | 0.1778 | 0.355 | 143.1 | 93.73 | 2.57
2026-04-11 16:00 | 1775937600 | 1 | 0.0861 | 0.17 | 149.29 | 95.05 | 1.352
2026-04-11 17:00 | 1775941200 | 1 | 0.0972 | 0.192 | 147.99 | 98.06 | 1.407
2026-04-11 18:00 | 1775944800 | 1 | 0.0917 | 0.181 | 147.83 | 99.31 | 1.29
2026-04-11 19:00 | 1775948400 | 1 | 0.1583 | 0.315 | 146.89 | 97.38 | 2.289
2026-04-11 20:00 | 1775952000 | 1 | 0.1389 | 0.278 | 145.87 | 105.02 | 1.667
2026-04-11 21:00 | 1775955600 | 1 | 0.1917 | 0.4 | 144.51 | 99.88 | 2.619
2026-04-11 22:00 | 1775959200 | 1 | 0.1611 | 0.307 | 140.8 | 100.26 | 1.826
2026-04-11 23:00 | 1775962800 | 1 | 0.0917 | 0.182 | 147.93 | 96.69 | 1.365
2026-04-12 00:00 | 1775966400 | 1 | 0.2778 | 0.513 | 143.17 | 97.89 | 3.403
2026-04-12 01:00 | 1775970000 | 1 | 0.1972 | 0.392 | 147.86 | 105.31 | 2.441
2026-04-12 02:00 | 1775973600 | 1 | 0.1972 | 0.355 | 146.85 | 102.8 | 2.291
2026-04-12 03:00 | 1775977200 | 1 | 0.2278 | 0.457 | 144.29 | 107.73 | 2.449
2026-04-12 04:00 | 1775980800 | 1 | 0.3722 | 0.755 | 141.81 | 104.79 | 4.095
2026-04-12 05:00 | 1775984400 | 1 | 0.3 | 0.664 | 138.08 | 106.99 | 3.026
2026-04-12 06:00 | 1775988000 | 1 | 0.3889 | 0.779 | 133.73 | 108.61 | 2.867
2026-04-12 07:00 | 1775991600 | 1 | 0.35 | 0.653 | 137.27 | 106.15 | 2.979
2026-04-12 08:00 | 1775995200 | 1 | 0.0944 | 0.189 | 142.37 | 101.13 | 1.14
2026-04-12 09:00 | 1775998800 | 1 | 0 | 0 |  |  | 0
2026-04-12 10:00 | 1776002400 | 1 | 0.0639 | 0.097 | 130.94 | 75.19 | 0.797
2026-04-12 11:00 | 1776006000 | 1 | 0 | 0 |  |  | 0
2026-04-12 12:00 | 1776009600 | 1 | 0 | 0 |  |  | 0
2026-04-12 13:00 | 1776013200 | 1 | 0 | 0 |  |  | 0
2026-04-12 14:00 | 1776016800 | 1 | 0.0917 | 0.182 | 138.18 | 82.14 | 1.498
2026-04-12 15:00 | 1776020400 | 1 | 0 | 0 |  |  | 0
2026-04-12 16:00 | 1776024000 | 1 | 0 | 0 |  |  | 0
2026-04-12 17:00 | 1776027600 | 1 | 0 | 0 |  |  | 0
2026-04-12 18:00 | 1776031200 | 1 | 0.0806 | 0.165 | 129.78 | 77.32 | 1.258
2026-04-12 19:00 | 1776034800 | 1 | 0 | 0 |  |  | 0
2026-04-12 20:00 | 1776038400 | 1 | 0 | 0 |  |  | 0
2026-04-12 21:00 | 1776042000 | 1 | 0.0806 | 0.16 | 141.23 | 79.02 | 1.454
2026-04-12 22:00 | 1776045600 | 0.9528 | 0 | 0 |  |  | 0
2026-04-12 23:00 | 1776049200 | 1 | 0.0917 | 0.183 | 144.53 | 93.9 | 1.36
2026-04-13 00:00 | 1776052800 | 1 | 0.0917 | 0.183 | 144.31 | 96.49 | 1.285
2026-04-13 01:00 | 1776056400 | 1 | 0.1944 | 0.392 | 144.51 | 99.76 | 2.574
2026-04-13 02:00 | 1776060000 | 1 | 0.0972 | 0.194 | 145.47 | 101.93 | 1.24
2026-04-13 03:00 | 1776063600 | 1 | 0.1833 | 0.369 | 147.57 | 99.99 | 2.567
2026-04-13 04:00 | 1776067200 | 1 | 0.1028 | 0.207 | 145.16 | 102.04 | 1.3
2026-04-13 05:00 | 1776070800 | 1 | 0.2667 | 0.502 | 140.12 | 98.56 | 3.06
2026-04-13 06:00 | 1776074400 | 1 | 0.1194 | 0.237 | 146.68 | 100.66 | 1.599
2026-04-13 07:00 | 1776078000 | 1 | 0.1667 | 0.333 | 152.08 | 103.2 | 2.385
2026-04-13 08:00 | 1776081600 | 1 | 0.1861 | 0.335 | 152.28 | 97.56 | 2.676
2026-04-13 09:00 | 1776085200 | 1 | 0.1778 | 0.354 | 149.96 | 104.92 | 2.338
2026-04-13 10:00 | 1776088800 | 1 | 0.2056 | 0.411 | 144.21 | 103.55 | 2.449
2026-04-13 11:00 | 1776092400 | 1 | 0.1028 | 0.209 | 143.33 | 102.14 | 1.253
2026-04-13 12:00 | 1776096000 | 1 | 0.2 | 0.479 | 142.94 | 95.97 | 3.296
2026-04-13 13:00 | 1776099600 | 1 | 0.0972 | 0.195 | 139.93 | 99.06 | 1.165
2026-04-13 14:00 | 1776103200 | 1 | 0 | 0 |  |  | 0
2026-04-13 15:00 | 1776106800 | 1 | 0 | 0 |  |  | 0
2026-04-13 16:00 | 1776110400 | 1 | 0.1917 | 0.347 | 132.88 | 87.53 | 2.303
2026-04-13 17:00 | 1776114000 | 1 | 0.0917 | 0.18 | 131.65 | 94.83 | 0.971
2026-04-13 18:00 | 1776117600 | 1 | 0.0917 | 0.182 | 120.44 | 85.09 | 0.944
2026-04-13 19:00 | 1776121200 | 1 | 0.0972 | 0.194 | 130.57 | 92.04 | 1.096
2026-04-13 20:00 | 1776124800 | 1 | 0.1417 | 0.257 | 126.58 | 79.91 | 1.755
2026-04-13 21:00 | 1776128400 | 1 | 0.0528 | 0.105 | 123.47 | 78.5 | 0.693
2026-04-13 22:00 | 1776132000 | 1 | 0.15 | 0.301 | 128.17 | 96.43 | 1.396
2026-04-13 23:00 | 1776135600 | 1 | 0.3778 | 0.755 | 114.36 | 97.17 | 1.902
2026-04-14 00:00 | 1776139200 | 1 | 0.7333 | 1.466 | 96.06 | 89.89 | 1.326
2026-04-14 01:00 | 1776142800 | 1 | 0.7694 | 1.536 | 123.76 | 109.63 | 3.18
2026-04-14 02:00 | 1776146400 | 1 | 0.8861 | 1.77 | 107.55 | 99.58 | 2.067
2026-04-14 03:00 | 1776150000 | 1 | 0.7694 | 1.54 | 111.59 | 101.22 | 2.342
2026-04-14 04:00 | 1776153600 | 1 | 0.7722 | 1.546 | 105.66 | 97.92 | 1.754
2026-04-14 05:00 | 1776157200 | 1 | 0.8972 | 1.795 | 100.17 | 94.02 | 1.616
2026-04-14 06:00 | 1776160800 | 1 | 1 | 2 | 97.49 | 90.33 | 2.099
2026-04-14 07:00 | 1776164400 | 1 | 0.4194 | 0.825 | 143.06 | 118.66 | 2.949
2026-04-14 08:00 | 1776168000 | 1 | 0 | 0 |  |  | 0
2026-04-14 09:00 | 1776171600 | 1 | 0.0861 | 0.173 | 130.34 | 83.99 | 1.165
2026-04-14 10:00 | 1776175200 | 1 | 0 | 0 |  |  | 0
2026-04-14 11:00 | 1776178800 | 1 | 0.0833 | 0.165 | 127.86 | 80.96 | 1.137
2026-04-14 12:00 | 1776182400 | 1 | 0 | 0 |  |  | 0
2026-04-14 13:00 | 1776186000 | 1 | 0 | 0 |  |  | 0
2026-04-14 14:00 | 1776189600 | 1 | 0 | 0 |  |  | 0
2026-04-14 15:00 | 1776193200 | 1 | 0 | 0 |  |  | 0
2026-04-14 16:00 | 1776196800 | 1 | 0.0194 | 0.035 | 107.35 | 62.6 | 0.231
2026-04-14 17:00 | 1776200400 | 1 | 0.0917 | 0.185 | 120.4 | 78.43 | 1.136
2026-04-14 18:00 | 1776204000 | 1 | 0.0861 | 0.171 | 121.42 | 84.15 | 0.935
2026-04-14 19:00 | 1776207600 | 1 | 0.0944 | 0.188 | 120.69 | 85.74 | 0.956
2026-04-14 20:00 | 1776211200 | 1 | 0.0889 | 0.177 | 120.42 | 85.65 | 0.901
2026-04-14 21:00 | 1776214800 | 1 | 0.0944 | 0.189 | 120.97 | 87.26 | 0.934
2026-04-14 22:00 | 1776218400 | 1 | 0.0944 | 0.189 | 117.8 | 88.16 | 0.82
2026-04-14 23:00 | 1776222000 | 1 | 0.0944 | 0.187 | 120.13 | 88.64 | 0.865
2026-04-15 00:00 | 1776225600 | 0.9972 | 0.2061 | 0.412 | 108.09 | 85.88 | 1.334
2026-04-15 01:00 | 1776229200 | 1 | 0.1 | 0.201 | 125.62 | 93.69 | 0.94
2026-04-15 02:00 | 1776232800 | 1 | 0.1861 | 0.367 | 123.29 | 90.55 | 1.763
2026-04-15 03:00 | 1776236400 | 1 | 0.0917 | 0.183 | 127.81 | 90.72 | 0.993
2026-04-15 04:00 | 1776240000 | 1 | 0.1 | 0.199 | 125.39 | 92.17 | 0.967
2026-04-15 05:00 | 1776243600 | 1 | 0.2028 | 0.406 | 116.85 | 90.97 | 1.531
2026-04-15 06:00 | 1776247200 | 1 | 0.1194 | 0.238 | 133.36 | 92.91 | 1.411
2026-04-15 07:00 | 1776250800 | 1 | 0.1611 | 0.321 | 134.34 | 95.24 | 1.834
2026-04-15 08:00 | 1776254400 | 1 | 0.0917 | 0.184 | 131.67 | 91.85 | 1.072
2026-04-15 09:00 | 1776258000 | 1 | 0.0917 | 0.179 | 131.61 | 91.82 | 1.045
2026-04-15 10:00 | 1776261600 | 1 | 0.0944 | 0.184 | 129.71 | 91.83 | 1.023
2026-04-15 11:00 | 1776265200 | 1 | 0.1889 | 0.373 | 125.72 | 91.2 | 1.887
2026-04-15 12:00 | 1776268800 | 1 | 0.0917 | 0.183 | 115.68 | 87.39 | 0.757
2026-04-15 13:00 | 1776272400 | 1 | 0.0889 | 0.175 | 106.92 | 85.03 | 0.562
2026-04-15 14:00 | 1776276000 | 1 | 0.1889 | 0.378 | 98.56 | 82.17 | 0.907
2026-04-15 15:00 | 1776279600 | 1 | 0.0972 | 0.188 | 94.52 | 80.85 | 0.374
2026-04-15 16:00 | 1776283200 | 1 | 0.3444 | 0.692 | 91.54 | 82.13 | 0.951
2026-04-15 17:00 | 1776286800 | 1 | 0.3917 | 0.781 | 85.12 | 79.83 | 0.606
2026-04-15 18:00 | 1776290400 | 1 | 0.725 | 1.445 | 81.86 | 78.89 | 0.629
2026-04-15 19:00 | 1776294000 | 1 | 0.3417 | 0.679 | 126.48 | 102.57 | 2.378
2026-04-15 20:00 | 1776297600 | 1 | 0.0861 | 0.17 | 126.11 | 84.79 | 1.027
2026-04-15 21:00 | 1776301200 | 1 | 0.0889 | 0.175 | 122.98 | 86.47 | 0.937
2026-04-15 22:00 | 1776304800 | 1 | 0.0917 | 0.186 | 131.39 | 90.71 | 1.102
2026-04-15 23:00 | 1776308400 | 1 | 0.0889 | 0.179 | 133.57 | 91.49 | 1.104
2026-04-16 00:00 | 1776312000 | 1 | 0.0861 | 0.174 | 131.62 | 90.84 | 1.035
2026-04-16 01:00 | 1776315600 | 1 | 0.1944 | 0.387 | 118.39 | 89.33 | 1.649
2026-04-16 02:00 | 1776319200 | 1 | 0.0917 | 0.183 | 138.24 | 94.89 | 1.162
2026-04-16 03:00 | 1776322800 | 1 | 0 | 0 |  |  | 0
2026-04-16 04:00 | 1776326400 | 1 | 0.0444 | 0.088 | 126.52 | 72.09 | 0.702
2026-04-16 05:00 | 1776330000 | 1 | 0.0361 | 0.072 | 138.47 | 90.96 | 0.504
2026-04-16 06:00 | 1776333600 | 1 | 0.0833 | 0.171 | 130.83 | 83.32 | 1.185
2026-04-16 07:00 | 1776337200 | 1 | 0.0861 | 0.172 | 126.3 | 84.32 | 1.059
2026-04-16 08:00 | 1776340800 | 1 | 0.0222 | 0.044 | 117.89 | 74.08 | 0.284
2026-04-16 09:00 | 1776344400 | 1 | 0.0583 | 0.116 | 135.47 | 86.31 | 0.836
2026-04-16 10:00 | 1776348000 | 1 | 0.0861 | 0.172 | 125.24 | 82.87 | 1.069
2026-04-16 11:00 | 1776351600 | 1 | 0.075 | 0.148 | 129.81 | 81.48 | 1.052
2026-04-16 12:00 | 1776355200 | 1 | 0.0028 | 0.006 | 134.38 | 102.78 | 0.03
2026-04-16 13:00 | 1776358800 | 1 | 0 | 0 |  |  | 0
2026-04-16 14:00 | 1776362400 | 1 | 0.0806 | 0.162 | 124.97 | 77.9 | 1.116
2026-04-16 15:00 | 1776366000 | 1 | 0.0833 | 0.166 | 125.12 | 81.41 | 1.06
2026-04-16 16:00 | 1776369600 | 1 | 0.0861 | 0.172 | 120.56 | 83.3 | 0.938
2026-04-16 17:00 | 1776373200 | 1 | 0.0889 | 0.177 | 127.27 | 86.92 | 1.044
2026-04-16 18:00 | 1776376800 | 1 | 0 | 0 |  |  | 0
2026-04-16 19:00 | 1776380400 | 1 | 0.0833 | 0.167 | 120.14 | 78.6 | 1.016
2026-04-16 20:00 | 1776384000 | 1 | 0 | 0 |  |  | 0.001
2026-04-16 21:00 | 1776387600 | 1 | 0.0806 | 0.161 | 116.35 | 76.44 | 0.942
2026-04-16 22:00 | 1776391200 | 1 | 0.0917 | 0.182 | 112.31 | 84.16 | 0.751
2026-04-16 23:00 | 1776394800 | 1 | 0.1972 | 0.394 | 113.16 | 89.17 | 1.386
2026-04-17 00:00 | 1776398400 | 1 | 0 | 0 |  |  | 0
2026-04-17 01:00 | 1776402000 | 1 | 0 | 0 |  |  | 0
2026-04-17 02:00 | 1776405600 | 1 | 0 | 0 |  |  | 0
2026-04-17 03:00 | 1776409200 | 1 | 0 | 0 |  |  | 0
2026-04-17 04:00 | 1776412800 | 1 | 0.0806 | 0.157 | 113.53 | 72.82 | 0.935
2026-04-17 05:00 | 1776416400 | 1 | 0.0833 | 0.167 | 114.85 | 77.49 | 0.906
2026-04-17 06:00 | 1776420000 | 1 | 0.0889 | 0.178 | 115.3 | 80.55 | 0.908
2026-04-17 07:00 | 1776423600 | 1 | 0 | 0 |  |  | 0
2026-04-17 08:00 | 1776427200 | 1 | 0.0861 | 0.172 | 117.87 | 78.76 | 0.981
2026-04-17 09:00 | 1776430800 | 1 | 0 | 0 |  |  | 0
2026-04-17 10:00 | 1776434400 | 1 | 0 | 0 |  |  | 0
2026-04-17 11:00 | 1776438000 | 1 | 0 | 0 |  |  | 0
2026-04-17 12:00 | 1776441600 | 1 | 0 | 0 |  |  | 0
2026-04-17 13:00 | 1776445200 | 1 | 0 | 0 |  |  | 0
2026-04-17 14:00 | 1776448800 | 1 | 0 | 0 |  |  | 0
2026-04-17 15:00 | 1776452400 | 1 | 0 | 0 |  |  | 0
2026-04-17 16:00 | 1776456000 | 1 | 0 | 0 |  |  | 0
2026-04-17 17:00 | 1776459600 | 1 | 0 | 0 |  |  | 0
2026-04-17 18:00 | 1776463200 | 1 | 0 | 0 |  |  | 0
2026-04-17 19:00 | 1776466800 | 1 | 0 | 0 |  |  | 0
2026-04-17 20:00 | 1776470400 | 1 | 0 | 0 |  |  | 0
2026-04-17 21:00 | 1776474000 | 1 | 0 | 0 |  |  | 0
2026-04-17 22:00 | 1776477600 | 1 | 0 | 0 |  |  | 0
2026-04-17 23:00 | 1776481200 | 1 | 0 | 0 |  |  | 0
2026-04-18 00:00 | 1776484800 | 1 | 0 | 0 |  |  | 0
2026-04-18 01:00 | 1776488400 | 1 | 0 | 0 |  |  | 0
2026-04-18 02:00 | 1776492000 | 1 | 0 | 0 |  |  | 0
2026-04-18 03:00 | 1776495600 | 1 | 0 | 0 |  |  | 0
2026-04-18 04:00 | 1776499200 | 1 | 0.0167 | 0.033 | 106.89 | 62.58 | 0.213
2026-04-18 05:00 | 1776502800 | 1 | 0.0917 | 0.182 | 120.87 | 79.36 | 1.107
2026-04-18 06:00 | 1776506400 | 1 | 0.0861 | 0.171 | 127.09 | 85.73 | 1.033
2026-04-18 07:00 | 1776510000 | 1 | 0.0833 | 0.166 | 130.23 | 84.39 | 1.114
2026-04-18 08:00 | 1776513600 | 1 | 0 | 0 |  |  | 0
2026-04-18 09:00 | 1776517200 | 1 | 0 | 0 |  |  | 0
2026-04-18 10:00 | 1776520800 | 1 | 0 | 0 |  |  | 0
2026-04-18 11:00 | 1776524400 | 1 | 0 | 0 |  |  | 0
2026-04-18 12:00 | 1776528000 | 1 | 0 | 0 |  |  | 0
2026-04-18 13:00 | 1776531600 | 1 | 0 | 0 |  |  | 0
2026-04-18 14:00 | 1776535200 | 1 | 0 | 0 |  |  | 0
2026-04-18 15:00 | 1776538800 | 1 | 0 | 0 |  |  | 0
2026-04-18 16:00 | 1776542400 | 1 | 0 | 0 |  |  | 0
2026-04-18 17:00 | 1776546000 | 1 | 0 | 0 |  |  | 0
2026-04-18 18:00 | 1776549600 | 1 | 0 | 0 |  |  | 0
2026-04-18 19:00 | 1776553200 | 1 | 0 | 0 |  |  | 0
2026-04-18 20:00 | 1776556800 | 1 | 0 | 0 |  |  | 0
2026-04-18 21:00 | 1776560400 | 1 | 0 | 0 |  |  | 0
2026-04-18 22:00 | 1776564000 | 1 | 0 | 0 |  |  | 0
2026-04-18 23:00 | 1776567600 | 1 | 0 | 0 |  |  | 0
2026-04-19 00:00 | 1776571200 | 1 | 0 | 0 |  |  | 0
2026-04-19 01:00 | 1776574800 | 1 | 0 | 0 |  |  | 0
2026-04-19 02:00 | 1776578400 | 1 | 0.0528 | 0.105 | 123.28 | 68.57 | 0.842
2026-04-19 03:00 | 1776582000 | 1 | 0.0944 | 0.189 | 125.05 | 81.3 | 1.214
2026-04-19 04:00 | 1776585600 | 1 | 0.1611 | 0.32 | 139.28 | 90.2 | 2.3
2026-04-19 05:00 | 1776589200 | 1 | 0.0861 | 0.171 | 139.76 | 90.43 | 1.239
2026-04-19 06:00 | 1776592800 | 1 | 0.0472 | 0.095 | 137.38 | 80.84 | 0.786
2026-04-19 07:00 | 1776596400 | 1 | 0.0944 | 0.189 | 141.96 | 90.6 | 1.423
2026-04-19 08:00 | 1776600000 | 1 | 0.0944 | 0.191 | 126.03 | 89.8 | 1.013
2026-04-19 09:00 | 1776603600 | 1 | 0.1083 | 0.22 | 129.23 | 90.66 | 1.232
2026-04-19 10:00 | 1776607200 | 1 | 0.0861 | 0.171 | 128.84 | 87.64 | 1.034
2026-04-19 11:00 | 1776610800 | 1 | 0.0917 | 0.182 | 128.16 | 89.22 | 1.041
2026-04-19 12:00 | 1776614400 | 1 | 0.0917 | 0.183 | 134.69 | 92.41 | 1.136
2026-04-19 13:00 | 1776618000 | 1 | 0.1722 | 0.343 | 131.72 | 89.77 | 2.11
2026-04-19 14:00 | 1776621600 | 1 | 0.1139 | 0.228 | 130.41 | 96.14 | 1.142
2026-04-19 15:00 | 1776625200 | 1 | 0.1639 | 0.328 | 130.25 | 93.18 | 1.779
2026-04-19 16:00 | 1776628800 | 1 | 0.1417 | 0.283 | 129.84 | 99.85 | 1.243
2026-04-19 17:00 | 1776632400 | 1 | 0.2083 | 0.419 | 129.52 | 98.49 | 1.904
2026-04-19 18:00 | 1776636000 | 1 | 0.2222 | 0.446 | 125.24 | 99.08 | 1.708
2026-04-19 19:00 | 1776639600 | 1 | 0.2556 | 0.509 | 129.86 | 99.05 | 2.3
2026-04-19 20:00 | 1776643200 | 1 | 0.3056 | 0.611 | 129.88 | 104.51 | 2.269
2026-04-19 21:00 | 1776646800 | 1 | 0.2389 | 0.478 | 128.24 | 102.95 | 1.771
2026-04-19 22:00 | 1776650400 | 1 | 0.3778 | 0.754 | 128.83 | 103.91 | 2.754
2026-04-19 23:00 | 1776654000 | 1 | 0.2222 | 0.44 | 139.37 | 105.19 | 2.206
2026-04-20 00:00 | 1776657600 | 1 | 0.2167 | 0.432 | 146.03 | 107.64 | 2.428
2026-04-20 01:00 | 1776661200 | 1 | 0.2056 | 0.418 | 148.96 | 106.52 | 2.591
2026-04-20 02:00 | 1776664800 | 1 | 0.2111 | 0.417 | 148.13 | 107.67 | 2.475
2026-04-20 03:00 | 1776668400 | 1 | 0.1833 | 0.363 | 138.39 | 104.02 | 1.826
2026-04-20 04:00 | 1776672000 | 1 | 0.2778 | 0.559 | 143.8 | 110.25 | 2.749
2026-04-20 05:00 | 1776675600 | 1 | 0.2222 | 0.443 | 144.5 | 109.76 | 2.256
2026-04-20 06:00 | 1776679200 | 1 | 0.5278 | 1.054 | 139.63 | 116.09 | 3.635
2026-04-20 07:00 | 1776682800 | 1 | 0.35 | 0.697 | 139.51 | 116.5 | 2.351
2026-04-20 08:00 | 1776686400 | 1 | 0.2222 | 0.446 | 146.24 | 106.68 | 2.578
2026-04-20 09:00 | 1776690000 | 1 | 0.1722 | 0.342 | 150.06 | 101.19 | 2.446
2026-04-20 10:00 | 1776693600 | 1 | 0.1194 | 0.237 | 147.42 | 106.05 | 1.435
2026-04-20 11:00 | 1776697200 | 1 | 0.1889 | 0.377 | 143.12 | 99.24 | 2.424
2026-04-20 12:00 | 1776700800 | 1 | 0 | 0 |  |  | 0
2026-04-20 13:00 | 1776704400 | 1 | 0 | 0 |  |  | 0
2026-04-20 14:00 | 1776708000 | 1 | 0 | 0 |  |  | 0
2026-04-20 15:00 | 1776711600 | 1 | 0.0806 | 0.16 | 137.35 | 78.86 | 1.374
2026-04-20 16:00 | 1776715200 | 1 | 0 | 0 |  |  | 0
2026-04-20 17:00 | 1776718800 | 1 | 0.1639 | 0.327 | 138.33 | 91.88 | 2.228
2026-04-20 18:00 | 1776722400 | 1 | 0.1528 | 0.304 | 140.18 | 103.17 | 1.648
2026-04-20 19:00 | 1776726000 | 1 | 0.1944 | 0.392 | 136.49 | 98.23 | 2.191
2026-04-20 20:00 | 1776729600 | 1 | 0 | 0 |  |  | 0
2026-04-20 21:00 | 1776733200 | 1 | 0.1806 | 0.36 | 140.58 | 92.23 | 2.548
2026-04-20 22:00 | 1776736800 | 1 | 0.2333 | 0.468 | 137.48 | 105.68 | 2.181
2026-04-20 23:00 | 1776740400 | 1 | 0.2917 | 0.582 | 136.13 | 108.7 | 2.331
2026-04-21 00:00 | 1776744000 | 1 | 0.4139 | 0.825 | 136.88 | 112.79 | 2.913
2026-04-21 01:00 | 1776747600 | 1 | 0.4222 | 0.849 | 145.42 | 115.92 | 3.661
2026-04-21 02:00 | 1776751200 | 1 | 0.3917 | 0.779 | 139.65 | 112.26 | 3.129
2026-04-21 03:00 | 1776754800 | 1 | 0.3611 | 0.723 | 143.8 | 116.08 | 2.935
2026-04-21 04:00 | 1776758400 | 1 | 0.4083 | 0.809 | 144.11 | 117.22 | 3.188
2026-04-21 05:00 | 1776762000 | 1 | 0.4722 | 0.946 | 137.65 | 114.91 | 3.146
2026-04-21 06:00 | 1776765600 | 1 | 0.5278 | 1.05 | 133.39 | 113.17 | 3.111
2026-04-21 07:00 | 1776769200 | 1 | 0.525 | 1.019 | 131 | 107.54 | 3.503
2026-04-21 08:00 | 1776772800 | 1 | 0.2333 | 0.47 | 126.53 | 101.97 | 1.682
2026-04-21 09:00 | 1776776400 | 1 | 0.2056 | 0.415 | 123.18 | 94.37 | 1.742
2026-04-21 10:00 | 1776780000 | 1 | 0.0917 | 0.189 | 121.37 | 90.36 | 0.846
2026-04-21 11:00 | 1776783600 | 1 | 0.1833 | 0.365 | 118.43 | 87.53 | 1.654
2026-04-21 12:00 | 1776787200 | 1 | 0 | 0 |  |  | 0
2026-04-21 13:00 | 1776790800 | 1 | 0.1889 | 0.376 | 125.48 | 86.65 | 2.138
2026-04-21 14:00 | 1776794400 | 1 | 0.0889 | 0.176 | 121.7 | 88.33 | 0.862
2026-04-21 15:00 | 1776798000 | 1 | 0.0861 | 0.172 | 133.28 | 87.23 | 1.16
2026-04-21 16:00 | 1776801600 | 1 | 0 | 0 |  |  | 0
2026-04-21 17:00 | 1776805200 | 1 | 0.0778 | 0.156 | 134.65 | 80.41 | 1.237
2026-04-21 18:00 | 1776808800 | 1 | 0.0917 | 0.182 | 142.53 | 92.08 | 1.342
2026-04-21 19:00 | 1776812400 | 1 | 0.175 | 0.348 | 142.23 | 94.62 | 2.429
2026-04-21 20:00 | 1776816000 | 1 | 0.0944 | 0.187 | 140.6 | 97.84 | 1.169
2026-04-21 21:00 | 1776819600 | 1 | 0.1889 | 0.378 | 138.05 | 98.5 | 2.188
2026-04-21 22:00 | 1776823200 | 1 | 0.0833 | 0.166 | 145.92 | 90.9 | 1.335
2026-04-21 23:00 | 1776826800 | 1 | 0.0917 | 0.183 | 135.82 | 91.86 | 1.179
2026-04-22 00:00 | 1776830400 | 0.9972 | 0.2061 | 0.411 | 134.74 | 100.12 | 2.077
2026-04-22 01:00 | 1776834000 | 1 | 0.2389 | 0.477 | 134.5 | 105.79 | 2.008
2026-04-22 02:00 | 1776837600 | 1 | 0.4 | 0.802 | 133.82 | 109.29 | 2.878
2026-04-22 03:00 | 1776841200 | 1 | 0.4833 | 0.963 | 131.3 | 110.15 | 2.984
2026-04-22 04:00 | 1776844800 | 1 | 0.4944 | 0.988 | 131.87 | 110.61 | 3.076
2026-04-22 05:00 | 1776848400 | 1 | 0.4528 | 0.907 | 135.94 | 113.16 | 3.019
2026-04-22 06:00 | 1776852000 | 1 | 0.4556 | 0.908 | 124.43 | 107.03 | 2.316
2026-04-22 07:00 | 1776855600 | 1 | 0.5861 | 1.17 | 120.08 | 106.96 | 2.251
2026-04-22 08:00 | 1776859200 | 1 | 0.7139 | 1.423 | 123.27 | 105.92 | 3.618
2026-04-22 09:00 | 1776862800 | 1 | 0.3306 | 0.662 | 140.39 | 115.33 | 2.424
2026-04-22 10:00 | 1776866400 | 1 | 0.2167 | 0.433 | 136.9 | 104.38 | 2.06
2026-04-22 11:00 | 1776870000 | 1 | 0.175 | 0.35 | 134.98 | 96.31 | 1.982
2026-04-22 12:00 | 1776873600 | 1 | 0.1139 | 0.235 | 131.59 | 100.29 | 1.071
2026-04-22 13:00 | 1776877200 | 1 | 0.2389 | 0.479 | 131.12 | 99.5 | 2.219
2026-04-22 14:00 | 1776880800 | 1 | 0.2389 | 0.475 | 130.93 | 101.06 | 2.081
2026-04-22 15:00 | 1776884400 | 1 | 0.5111 | 1.021 | 115.45 | 101.27 | 2.116
2026-04-22 16:00 | 1776888000 | 1 | 0.3889 | 0.775 | 110.23 | 95.95 | 1.622
2026-04-22 17:00 | 1776891600 | 1 | 0.6889 | 1.372 | 112.04 | 99.8 | 2.461
2026-04-22 18:00 | 1776895200 | 1 | 0.5861 | 1.164 | 135.08 | 115.72 | 3.302
2026-04-22 19:00 | 1776898800 | 1 | 0.5083 | 1.013 | 128.43 | 112.83 | 2.316
2026-04-22 20:00 | 1776902400 | 1 | 0.2222 | 0.442 | 125.46 | 100.28 | 1.629
2026-04-22 21:00 | 1776906000 | 1 | 0.4056 | 0.811 | 124.34 | 103.7 | 2.448
2026-04-22 22:00 | 1776909600 | 0.9556 | 0.689 | 1.375 | 125.98 | 109.04 | 3.261
2026-04-22 23:00 | 1776913200 | 1 | 0.5556 | 1.115 | 115.79 | 104.02 | 1.922
2026-04-23 00:00 | 1776916800 | 1 | 0.8944 | 1.785 | 110.61 | 100.64 | 2.608
2026-04-23 01:00 | 1776920400 | 1 | 0.7528 | 1.492 | 131.51 | 116.78 | 3.221
2026-04-23 02:00 | 1776924000 | 1 | 0.5639 | 1.122 | 126.06 | 111.79 | 2.344
2026-04-23 03:00 | 1776927600 | 1 | 0.7222 | 1.446 | 114.96 | 103.24 | 2.482
2026-04-23 04:00 | 1776931200 | 1 | 0.7556 | 1.507 | 112.08 | 100.87 | 2.474
2026-04-23 05:00 | 1776934800 | 1 | 0.525 | 1.04 | 135.65 | 118.1 | 2.673
2026-04-23 06:00 | 1776938400 | 1 | 0.575 | 1.147 | 116.98 | 103.92 | 2.195
2026-04-23 07:00 | 1776942000 | 1 | 0.6389 | 1.273 | 120.54 | 105.98 | 2.718
2026-04-23 08:00 | 1776945600 | 1 | 0.7222 | 1.445 | 109.8 | 100.62 | 1.946
2026-04-23 09:00 | 1776949200 | 1 | 1 | 1.999 | 106.83 | 99.38 | 2.183
2026-04-23 10:00 | 1776952800 | 1 | 1 | 1.996 | 107.6 | 100.16 | 2.174
2026-04-23 11:00 | 1776956400 | 1 | 1 | 2.001 | 103.85 | 97.37 | 1.897
2026-04-23 12:00 | 1776960000 | 1 | 1 | 1.992 | 127.57 | 113.39 | 4.137
2026-04-23 13:00 | 1776963600 | 1 | 0.4417 | 0.884 | 134.89 | 117.31 | 2.272
2026-04-23 14:00 | 1776967200 | 1 | 0.1 | 0.198 | 136.19 | 96.69 | 1.149
2026-04-23 15:00 | 1776970800 | 1 | 0.1917 | 0.384 | 132.72 | 96.32 | 2.047
2026-04-23 16:00 | 1776974400 | 1 | 0.2083 | 0.416 | 141.41 | 102.54 | 2.371
2026-04-23 17:00 | 1776978000 | 1 | 0.1944 | 0.386 | 147.75 | 104.32 | 2.456
2026-04-23 18:00 | 1776981600 | 1 | 0.1 | 0.2 | 146.15 | 104.7 | 1.213
2026-04-23 19:00 | 1776985200 | 1 | 0.0944 | 0.186 | 140.43 | 102.3 | 1.04
2026-04-23 20:00 | 1776988800 | 1 | 0 | 0 |  |  | 0
2026-04-23 21:00 | 1776992400 | 1 | 0.0861 | 0.172 | 126.44 | 81.12 | 1.141
2026-04-23 22:00 | 1776996000 | 1 | 0.2139 | 0.426 | 130.1 | 97.39 | 2.044
2026-04-23 23:00 | 1776999600 | 1 | 0.4278 | 0.855 | 131.57 | 107.83 | 2.97
2026-04-24 00:00 | 1777003200 | 1 | 0.4833 | 0.96 | 133.96 | 112.54 | 3.013
2026-04-24 01:00 | 1777006800 | 1 | 0.5361 | 1.065 | 133.68 | 113.98 | 3.073
2026-04-24 02:00 | 1777010400 | 1 | 0.5444 | 1.087 | 127.45 | 111.19 | 2.587
2026-04-24 03:00 | 1777014000 | 1 | 0.5694 | 1.135 | 133.6 | 115.59 | 2.991
2026-04-24 04:00 | 1777017600 | 1 | 0.2556 | 0.51 | 130.85 | 110.13 | 1.549
2026-04-24 05:00 | 1777021200 | 1 | 0.1861 | 0.37 | 150.06 | 101.22 | 2.645
2026-04-24 06:00 | 1777024800 | 1 | 0.0972 | 0.194 | 146.83 | 102.93 | 1.248
2026-04-24 07:00 | 1777028400 | 1 | 0.1917 | 0.381 | 143.62 | 101.38 | 2.357
2026-04-24 08:00 | 1777032000 | 1 | 0.0889 | 0.177 | 140.86 | 95.2 | 1.184
2026-04-24 09:00 | 1777035600 | 1 | 0.2111 | 0.421 | 139.4 | 101.3 | 2.349
2026-04-24 10:00 | 1777039200 | 1 | 0.2167 | 0.432 | 139.03 | 102.66 | 2.304
2026-04-24 11:00 | 1777042800 | 1 | 0.2028 | 0.405 | 135.95 | 100.86 | 2.08
2026-04-24 12:00 | 1777046400 | 1 | 0.2083 | 0.417 | 141.12 | 102.66 | 2.349
2026-04-24 13:00 | 1777050000 | 1 | 0.1 | 0.198 | 135.61 | 99.02 | 1.063
2026-04-24 14:00 | 1777053600 | 1 | 0.3111 | 0.616 | 126.11 | 99.11 | 2.438
2026-04-24 15:00 | 1777057200 | 1 | 0.1056 | 0.21 | 133.11 | 99.43 | 1.035
2026-04-24 16:00 | 1777060800 | 1 | 0.1889 | 0.375 | 148.94 | 101.61 | 2.603
2026-04-24 17:00 | 1777064400 | 1 | 0.0889 | 0.177 | 150.48 | 99.75 | 1.313
2026-04-24 18:00 | 1777068000 | 1 | 0.1944 | 0.385 | 147.06 | 101 | 2.596
2026-04-24 19:00 | 1777071600 | 1 | 0.1694 | 0.336 | 143.85 | 100.41 | 2.14
2026-04-24 20:00 | 1777075200 | 1 | 0.1861 | 0.37 | 141.32 | 104.62 | 1.99
2026-04-24 21:00 | 1777078800 | 1 | 0.2 | 0.398 | 137.95 | 104.02 | 1.978
2026-04-24 22:00 | 1777082400 | 1 | 0.2722 | 0.544 | 136.26 | 104.39 | 2.541
2026-04-24 23:00 | 1777086000 | 1 | 0.2194 | 0.438 | 132.65 | 103.4 | 1.875
2026-04-25 00:00 | 1777089600 | 1 | 0.2194 | 0.44 | 138.58 | 105.93 | 2.099
2026-04-25 01:00 | 1777093200 | 1 | 0.2167 | 0.435 | 132.23 | 102.83 | 1.872
2026-04-25 02:00 | 1777096800 | 1 | 0.2694 | 0.537 | 132.63 | 102.75 | 2.345
2026-04-25 03:00 | 1777100400 | 0.9694 | 0.1862 | 0.371 | 135.58 | 107.91 | 1.453
2026-04-25 04:00 | 1777104000 | 0.9806 | 0.255 | 0.513 | 130.82 | 103.34 | 2.023
2026-04-25 05:00 | 1777107600 | 1 | 0.35 | 0.699 | 135.21 | 107.08 | 2.88
2026-04-25 06:00 | 1777111200 | 1 | 0.2167 | 0.431 | 133.74 | 105.29 | 1.798
2026-04-25 07:00 | 1777114800 | 1 | 0.2028 | 0.407 | 130.57 | 100.13 | 1.814
2026-04-25 08:00 | 1777118400 | 1 | 0.0861 | 0.173 | 127.46 | 90.06 | 0.95
2026-04-25 09:00 | 1777122000 | 1 | 0.1889 | 0.374 | 125.42 | 91.69 | 1.85
2026-04-25 10:00 | 1777125600 | 1 | 0.1528 | 0.307 | 125.54 | 94.53 | 1.388
2026-04-25 11:00 | 1777129200 | 1 | 0.15 | 0.304 | 125.75 | 93.96 | 1.406
2026-04-25 12:00 | 1777132800 | 1 | 0 | 0 |  |  | 0
2026-04-25 13:00 | 1777136400 | 1 | 0.0806 | 0.163 | 120.6 | 79.35 | 0.982
2026-04-25 14:00 | 1777140000 | 1 | 0 | 0 |  |  | 0
2026-04-25 15:00 | 1777143600 | 1 | 0.0861 | 0.171 | 128.76 | 81.78 | 1.18
2026-04-25 16:00 | 1777147200 | 1 | 0 | 0 |  |  | 0
2026-04-25 17:00 | 1777150800 | 1 | 0 | 0 |  |  | 0
2026-04-25 18:00 | 1777154400 | 1 | 0.0861 | 0.171 | 122.02 | 79.13 | 1.076
2026-04-25 19:00 | 1777158000 | 1 | 0.0861 | 0.172 | 138.32 | 86.96 | 1.293
2026-04-25 20:00 | 1777161600 | 1 | 0.0917 | 0.184 | 141.56 | 91.4 | 1.345
2026-04-25 21:00 | 1777165200 | 1 | 0.0861 | 0.171 | 141.01 | 90.26 | 1.272
2026-04-25 22:00 | 1777168800 | 1 | 0.0861 | 0.171 | 142.22 | 92.51 | 1.248
2026-04-25 23:00 | 1777172400 | 1 | 0.0972 | 0.193 | 144.96 | 101.57 | 1.229
2026-04-26 00:00 | 1777176000 | 1 | 0.1833 | 0.369 | 139.2 | 95.69 | 2.344
2026-04-26 01:00 | 1777179600 | 1 | 0.0972 | 0.193 | 138.22 | 99.16 | 1.105
2026-04-26 02:00 | 1777183200 | 1 | 0.2 | 0.398 | 136.1 | 99.12 | 2.156
2026-04-26 03:00 | 1777186800 | 1 | 0.2028 | 0.403 | 139.04 | 102.28 | 2.173
2026-04-26 04:00 | 1777190400 | 1 | 0.2278 | 0.455 | 130.28 | 102.8 | 1.832
2026-04-26 05:00 | 1777194000 | 1 | 0.2306 | 0.459 | 129.49 | 103.24 | 1.767
2026-04-26 06:00 | 1777197600 | 1 | 0.3333 | 0.664 | 129.88 | 104.09 | 2.508
2026-04-26 07:00 | 1777201200 | 0.9528 | 0.2303 | 0.459 | 128.73 | 95.79 | 2.11
2026-04-26 08:00 | 1777204800 | 1 | 0.0861 | 0.172 | 126.47 | 92.71 | 0.851
2026-04-26 09:00 | 1777208400 | 1 | 0 | 0 |  |  | 0
2026-04-26 10:00 | 1777212000 | 1 | 0 | 0 |  |  | 0
2026-04-26 11:00 | 1777215600 | 1 | 0 | 0 |  |  | 0
2026-04-26 12:00 | 1777219200 | 1 | 0 | 0 |  |  | 0
2026-04-26 13:00 | 1777222800 | 1 | 0.0111 | 0.022 | 92.9 | 64.96 | 0.09
2026-04-26 14:00 | 1777226400 | 1 | 0.1778 | 0.357 | 117.23 | 83.92 | 1.74
2026-04-26 15:00 | 1777230000 | 1 | 0.2167 | 0.432 | 110.49 | 92.1 | 1.165
2026-04-26 16:00 | 1777233600 | 1 | 0.3806 | 0.765 | 101.87 | 90.46 | 1.279
2026-04-26 17:00 | 1777237200 | 1 | 0.3833 | 0.765 | 90.8 | 85.82 | 0.559
2026-04-26 18:00 | 1777240800 | 1 | 0 | 0 |  |  | 0
2026-04-26 19:00 | 1777244400 | 1 | 0 | 0 |  |  | 0
2026-04-26 20:00 | 1777248000 | 1 | 0 | 0 |  |  | 0
2026-04-26 21:00 | 1777251600 | 1 | 0 | 0 |  |  | 0
2026-04-26 22:00 | 1777255200 | 1 | 0 | 0 |  |  | 0
2026-04-26 23:00 | 1777258800 | 1 | 0 | 0 |  |  | 0
2026-04-27 00:00 | 1777262400 | 1 | 0 | 0 |  |  | 0
2026-04-27 01:00 | 1777266000 | 1 | 0 | 0 |  |  | 0
2026-04-27 02:00 | 1777269600 | 1 | 0 | 0 |  |  | 0
2026-04-27 03:00 | 1777273200 | 1 | 0 | 0 |  |  | 0
2026-04-27 04:00 | 1777276800 | 1 | 0 | 0 |  |  | 0
2026-04-27 05:00 | 1777280400 | 1 | 0 | 0 |  |  | 0
2026-04-27 06:00 | 1777284000 | 1 | 0 | 0 |  |  | 0
2026-04-27 07:00 | 1777287600 | 1 | 0 | 0 |  |  | 0
2026-04-27 08:00 | 1777291200 | 1 | 0 | 0 |  |  | 0
2026-04-27 09:00 | 1777294800 | 1 | 0 | 0 |  |  | 0
2026-04-27 10:00 | 1777298400 | 1 | 0 | 0 |  |  | 0
2026-04-27 11:00 | 1777302000 | 1 | 0 | 0 |  |  | 0
2026-04-27 12:00 | 1777305600 | 1 | 0 | 0 |  |  | 0
2026-04-27 13:00 | 1777309200 | 1 | 0 | 0 |  |  | 0
2026-04-27 14:00 | 1777312800 | 1 | 0 | 0 |  |  | 0
2026-04-27 15:00 | 1777316400 | 1 | 0 | 0 |  |  | 0
2026-04-27 16:00 | 1777320000 | 1 | 0 | 0 |  |  | 0
2026-04-27 17:00 | 1777323600 | 1 | 0 | 0 |  |  | 0
2026-04-27 18:00 | 1777327200 | 1 | 0 | 0 |  |  | 0
2026-04-27 19:00 | 1777330800 | 1 | 0 | 0 |  |  | 0
2026-04-27 20:00 | 1777334400 | 1 | 0 | 0 |  |  | 0
2026-04-27 21:00 | 1777338000 | 1 | 0 | 0 |  |  | 0
2026-04-27 22:00 | 1777341600 | 1 | 0 | 0 |  |  | 0
2026-04-27 23:00 | 1777345200 | 1 | 0 | 0 |  |  | 0
2026-04-28 00:00 | 1777348800 | 1 | 0 | 0 |  |  | 0
2026-04-28 01:00 | 1777352400 | 1 | 0 | 0 |  |  | 0
2026-04-28 02:00 | 1777356000 | 1 | 0 | 0 |  |  | 0
2026-04-28 03:00 | 1777359600 | 1 | 0 | 0 |  |  | 0
2026-04-28 04:00 | 1777363200 | 1 | 0 | 0 |  |  | 0
2026-04-28 05:00 | 1777366800 | 1 | 0 | 0 |  |  | 0
2026-04-28 06:00 | 1777370400 | 1 | 0 | 0 |  |  | 0
2026-04-28 07:00 | 1777374000 | 1 | 0 | 0 |  |  | 0
2026-04-28 08:00 | 1777377600 | 1 | 0 | 0 |  |  | 0
2026-04-28 09:00 | 1777381200 | 1 | 0 | 0 |  |  | 0
2026-04-28 10:00 | 1777384800 | 1 | 0 | 0 |  |  | 0
2026-04-28 11:00 | 1777388400 | 1 | 0 | 0 |  |  | 0
2026-04-28 12:00 | 1777392000 | 1 | 0 | 0 |  |  | 0
2026-04-28 13:00 | 1777395600 | 1 | 0 | 0 |  |  | 0
2026-04-28 14:00 | 1777399200 | 1 | 0 | 0 |  |  | 0
2026-04-28 15:00 | 1777402800 | 1 | 0 | 0 |  |  | 0
2026-04-28 16:00 | 1777406400 | 1 | 0 | 0 |  |  | 0
2026-04-28 17:00 | 1777410000 | 1 | 0 | 0 |  |  | 0
2026-04-28 18:00 | 1777413600 | 1 | 0 | 0 |  |  | 0
2026-04-28 19:00 | 1777417200 | 1 | 0 | 0 |  |  | 0
2026-04-28 20:00 | 1777420800 | 1 | 0.0611 | 0.121 | 105.42 | 66.38 | 0.694
2026-04-28 21:00 | 1777424400 | 1 | 0.0778 | 0.154 | 126.11 | 83.34 | 0.966
2026-04-28 22:00 | 1777428000 | 1 | 0.0806 | 0.161 | 124.36 | 80.21 | 1.044
2026-04-28 23:00 | 1777431600 | 1 | 0.0861 | 0.173 | 128.84 | 86.31 | 1.079
2026-04-29 00:00 | 1777435200 | 0.9694 | 0.0888 | 0.177 | 129.16 | 87.87 | 1.041
2026-04-29 01:00 | 1777438800 | 1 | 0.1361 | 0.271 | 116.75 | 84.77 | 1.269
2026-04-29 02:00 | 1777442400 | 1 | 0.1472 | 0.293 | 124.03 | 94.51 | 1.266
2026-04-29 03:00 | 1777446000 | 1 | 0.2389 | 0.477 | 116.94 | 92.55 | 1.703
2026-04-29 04:00 | 1777449600 | 1 | 0.2778 | 0.554 | 128.65 | 98.67 | 2.434
2026-04-29 05:00 | 1777453200 | 1 | 0.1056 | 0.216 | 134.55 | 101.39 | 1.036
2026-04-29 06:00 | 1777456800 | 1 | 0.3444 | 0.684 | 115.03 | 95.77 | 1.932
2026-04-29 07:00 | 1777460400 | 1 | 0.2722 | 0.547 | 118.28 | 97.62 | 1.654
2026-04-29 08:00 | 1777464000 | 1 | 0.2944 | 0.586 | 113.85 | 95.18 | 1.605
2026-04-29 09:00 | 1777467600 | 1 | 0.2389 | 0.477 | 109.35 | 93.39 | 1.115
2026-04-29 10:00 | 1777471200 | 1 | 0.2083 | 0.414 | 126.73 | 92.51 | 2.077
2026-04-29 11:00 | 1777474800 | 1 | 0.0806 | 0.16 | 141.74 | 90.52 | 1.2
2026-04-29 12:00 | 1777478400 | 1 | 0 | 0 |  |  | 0
2026-04-29 13:00 | 1777482000 | 1 | 0 | 0 |  |  | 0
2026-04-29 14:00 | 1777485600 | 1 | 0.0417 | 0.083 | 139.44 | 73.13 | 0.802
2026-04-29 15:00 | 1777489200 | 1 | 0 | 0 |  |  | 0
2026-04-29 16:00 | 1777492800 | 1 | 0.0611 | 0.124 | 139.59 | 74.97 | 1.17
2026-04-29 17:00 | 1777496400 | 1 | 0.25 | 0.497 | 146.67 | 113.99 | 2.379
2026-04-29 18:00 | 1777500000 | 1 | 0.225 | 0.446 | 145.02 | 110.05 | 2.287
2026-04-29 19:00 | 1777503600 | 1 | 0 | 0 |  |  | 0
2026-04-29 20:00 | 1777507200 | 1 | 0 | 0 |  |  | 0
2026-04-29 21:00 | 1777510800 | 1 | 0.0861 | 0.17 | 128.05 | 81.33 | 1.166
2026-04-29 22:00 | 1777514400 | 1 | 0.0861 | 0.17 | 141.84 | 91.63 | 1.254
2026-04-29 23:00 | 1777518000 | 1 | 0.1778 | 0.354 | 144.45 | 96.15 | 2.495
2026-04-30 00:00 | 1777521600 | 1 | 0.0917 | 0.181 | 144.83 | 98.59 | 1.226
2026-04-30 01:00 | 1777525200 | 1 | 0.0972 | 0.192 | 144.93 | 98.94 | 1.293
2026-04-30 02:00 | 1777528800 | 1 | 0.1889 | 0.377 | 141.13 | 98.32 | 2.357
2026-04-30 03:00 | 1777532400 | 1 | 0.0972 | 0.193 | 140.28 | 98.59 | 1.178
2026-04-30 04:00 | 1777536000 | 1 | 0.1944 | 0.388 | 139.61 | 99.47 | 2.281
2026-04-30 05:00 | 1777539600 | 1 | 0.0917 | 0.182 | 136.64 | 99.13 | 0.999
2026-04-30 06:00 | 1777543200 | 1 | 0.2167 | 0.432 | 126.43 | 98.29 | 1.781
2026-04-30 07:00 | 1777546800 | 1 | 0.2167 | 0.411 | 133.52 | 100.27 | 1.999
2026-04-30 08:00 | 1777550400 | 1 | 0.1944 | 0.385 | 129.25 | 96.57 | 1.841
2026-04-30 09:00 | 1777554000 | 1 | 0.1028 | 0.206 | 129.88 | 97.02 | 0.992
2026-04-30 10:00 | 1777557600 | 1 | 0.1972 | 0.392 | 128.39 | 96.43 | 1.834
2026-04-30 11:00 | 1777561200 | 1 | 0.1917 | 0.382 | 128.27 | 96.08 | 1.802
2026-04-30 12:00 | 1777564800 | 1 | 0.1 | 0.199 | 124.58 | 95.55 | 0.845
2026-04-30 13:00 | 1777568400 | 1 | 0.1944 | 0.389 | 127.56 | 96.52 | 1.76
2026-04-30 14:00 | 1777572000 | 1 | 0.2056 | 0.409 | 126.78 | 98.6 | 1.686
2026-04-30 15:00 | 1777575600 | 1 | 0.1194 | 0.245 | 128.98 | 92.68 | 1.297
2026-04-30 16:00 | 1777579200 | 1 | 0.1722 | 0.343 | 123.21 | 96.27 | 1.355
2026-04-30 17:00 | 1777582800 | 1 | 0.3167 | 0.627 | 114.27 | 94.77 | 1.792
2026-04-30 18:00 | 1777586400 | 1 | 0.2556 | 0.508 | 110.2 | 94.81 | 1.146
2026-04-30 19:00 | 1777590000 | 1 | 0.0917 | 0.183 | 104.03 | 86.55 | 0.469
2026-04-30 20:00 | 1777593600 | 1 | 0.0806 | 0.161 | 99.47 | 78.46 | 0.495
2026-04-30 21:00 | 1777597200 | 1 | 0.0722 | 0.144 | 128.16 | 82.68 | 0.957
2026-04-30 22:00 | 1777600800 | 1 | 0 | 0 |  |  | 0
2026-04-30 23:00 | 1777604400 | 1 | 0 | 0 |  |  | 0