## Summary
cold-zone-call-during-steady-heating-memo
Beech's distribution loop when an idle zone calls inside a steady call: the minute trace around the 2026-01-26 06:17 call, the season's 45 such calls with their recovery and the cold water each returned, the drop's later movement against control minutes, the slug as a volume, and the steady hours the source-drop line comes from. Every cell is one number; the README in the experiments folder says how each table was made.
Tab | What the rows are | Rows | Columns | Produced by
beech-2026-01-26-minutes | Beech 2026-01-26, 05:45 to 07:15 ET: the minute trace around the 06:17 upstairs call | 90 | 10 | pump_speed.py
beech-cold-zone-events | beech: each idle-zone call inside a steady call, its recovery and the cold water it returned | 45 | 11 | bolus_recovery.py
beech-cold-zone-excess | beech: the drop's excess over its pre-call value by minute after the call, against control minutes; detrended = the steady line's share of the source's move removed (slope 0.234 F per F) | 4 | 13 | bolus_recovery.py
beech-cold-zone-slug-volume | beech: the idle loop's cold water as a volume at the slug temperature, quartiles over the calls | 3 | 4 | bolus_recovery.py
beech-steady-drop | Beech steady-circulation hours by source temperature bin: drop quartiles, median flow, median heat | 5 | 9 | steady_drop.py

## beech-2026-01-26-minutes
MinuteStartEt | MinuteStartS | Gpm | PumpW | Pump010V | SourceF | ReturnF | TempAgeS | zone1-down-whitewire-pwr | zone2-up-whitewire-pwr
2026-01-26 05:45 | 1769424300 | 2.02 | 7 | 3.5 | 121.23 | 108.78 | 50 | 1 | 0
2026-01-26 05:46 | 1769424360 | 2.02 | 7 | 3.5 | 122.26 | 108.85 | 100 | 1 | 0
2026-01-26 05:47 | 1769424420 | 2.02 | 7 | 3.5 | 123.39 | 109.23 | 56 | 1 | 0
2026-01-26 05:48 | 1769424480 | 2.02 | 7 | 3.5 | 118.3 | 109.54 | 64 | 1 | 0
2026-01-26 05:49 | 1769424540 | 2.02 | 7 | 3.5 | 111.7 | 109.8 | 84 | 1 | 0
2026-01-26 05:50 | 1769424600 | 2.02 | 7 | 3.5 | 113.39 | 109.39 | 49 | 1 | 0
2026-01-26 05:51 | 1769424660 | 2.02 | 7 | 3.5 | 113.7 | 108.4 | 87 | 1 | 0
2026-01-26 05:52 | 1769424720 | 2.02 | 7 | 3.5 | 112.99 | 107.83 | 97 | 1 | 0
2026-01-26 05:53 | 1769424780 | 2.02 | 7 | 3.5 | 112.53 | 105.97 | 82 | 1 | 0
2026-01-26 05:54 | 1769424840 | 2.02 | 7 | 3.5 | 112.09 | 104.73 | 92 | 1 | 0
2026-01-26 05:55 | 1769424900 | 2.022 | 7.5 | 3.5 | 111.52 | 104.31 | 50 | 1 | 0
2026-01-26 05:56 | 1769424960 | 2.02 | 8 | 3.5 | 113.8 | 103.94 | 60 | 1 | 0
2026-01-26 05:57 | 1769425020 | 2.02 | 8 | 3.5 | 121.27 | 103.57 | 63 | 1 | 0
2026-01-26 05:58 | 1769425080 | 2.02 | 8 | 3.5 | 125.05 | 103.63 | 113 | 1 | 0
2026-01-26 05:59 | 1769425140 | 2.02 | 8 | 3.5 | 127.53 | 104.54 | 17 | 1 | 0
2026-01-26 06:00 | 1769425200 | 2.012 | 8 | 3.5 | 128.74 | 105.91 | 50 | 1 | 0
2026-01-26 06:01 | 1769425260 | 2.01 | 8 | 3.5 | 129.68 | 108.38 | 60 | 1 | 0
2026-01-26 06:02 | 1769425320 | 2.01 | 8 | 3.5 | 130.15 | 110.79 | 46 | 1 | 0
2026-01-26 06:03 | 1769425380 | 2.01 | 8 | 3.5 | 131.86 | 112.71 | 14 | 1 | 0
2026-01-26 06:04 | 1769425440 | 2.01 | 8 | 3.5 | 134.79 | 114.21 | 22 | 1 | 0
2026-01-26 06:05 | 1769425500 | 2.018 | 8 | 3.5 | 135.57 | 115.3 | 32 | 1 | 0
2026-01-26 06:06 | 1769425560 | 2.02 | 8 | 3.5 | 136.3 | 116.39 | 30 | 1 | 0
2026-01-26 06:07 | 1769425620 | 2.02 | 8 | 3.5 | 136.99 | 117.26 | 38 | 1 | 0
2026-01-26 06:08 | 1769425680 | 2.02 | 8 | 3.5 | 137.54 | 118.45 | 40 | 1 | 0
2026-01-26 06:09 | 1769425740 | 2.02 | 8 | 3.5 | 138.11 | 119.41 | 36 | 1 | 0
2026-01-26 06:10 | 1769425800 | 2.012 | 7.5 | 3.5 | 138.67 | 120.16 | 40 | 1 | 0
2026-01-26 06:11 | 1769425860 | 2.01 | 7 | 3.5 | 139.07 | 120.75 | 57 | 1 | 0
2026-01-26 06:12 | 1769425920 | 2.01 | 7 | 3.5 | 139.43 | 121.31 | 60 | 1 | 0
2026-01-26 06:13 | 1769425980 | 2.01 | 7 | 3.5 | 139.75 | 121.74 | 62 | 1 | 0
2026-01-26 06:14 | 1769426040 | 2.01 | 7 | 3.5 | 139.49 | 122.12 | 92 | 1 | 0
2026-01-26 06:15 | 1769426100 | 2.01 | 7 | 3.5 | 138.91 | 122.46 | 50 | 1 | 0
2026-01-26 06:16 | 1769426160 | 2.01 | 7 | 3.5 | 140.51 | 122.61 | 90 | 1 | 0
2026-01-26 06:17 | 1769426220 | 2.547 | 8 | 3.5 | 141.05 | 119.76 | 59 | 1 | 1
2026-01-26 06:18 | 1769426280 | 3.15 | 9 | 3.5 | 139.63 | 104.51 | 47 | 1 | 1
2026-01-26 06:19 | 1769426340 | 3.15 | 9 | 3.5 | 131.23 | 100.62 | 14 | 1 | 1
2026-01-26 06:20 | 1769426400 | 3.192 | 9 | 3.5 | 129.11 | 108.09 | 11 | 1 | 1
2026-01-26 06:21 | 1769426460 | 3.2 | 9 | 3.5 | 133.87 | 112.12 | 24 | 1 | 1
2026-01-26 06:22 | 1769426520 | 3.2 | 8.5 | 3.5 | 136.05 | 112.36 | 74 | 1 | 1
2026-01-26 06:23 | 1769426580 | 2.25 | 8 | 3.5 | 136.11 | 116.06 | 105 | 1 | 0
2026-01-26 06:24 | 1769426640 | 2.06 | 8 | 3.5 | 137.72 | 117.99 | 60 | 1 | 0
2026-01-26 06:25 | 1769426700 | 2.018 | 8 | 3.5 | 139 | 118.03 | 70 | 1 | 0
2026-01-26 06:26 | 1769426760 | 2.01 | 8 | 3.5 | 139.03 | 119.24 | 110 | 1 | 0
2026-01-26 06:27 | 1769426820 | 2.01 | 7.5 | 3.5 | 139.45 | 120.43 | 120 | 1 | 0
2026-01-26 06:28 | 1769426880 | 2.01 | 7 | 3.5 | 140.08 | 121.23 | 42 | 1 | 0
2026-01-26 06:29 | 1769426940 | 2.01 | 7 | 3.5 | 140.21 | 122 | 92 | 1 | 0
2026-01-26 06:30 | 1769427000 | 2.018 | 7 | 3.5 | 140.72 | 122.58 | 50 | 1 | 0
2026-01-26 06:31 | 1769427060 | 2.02 | 7 | 3.5 | 140.88 | 122.92 | 90 | 1 | 0
2026-01-26 06:32 | 1769427120 | 2.02 | 7 | 3.5 | 141.52 | 123.3 | 56 | 1 | 0
2026-01-26 06:33 | 1769427180 | 2.02 | 7 | 3.5 | 142.46 | 123.5 | 86 | 1 | 0
2026-01-26 06:34 | 1769427240 | 2.02 | 7 | 3.5 | 143.04 | 123.83 | 70 | 1 | 0
2026-01-26 06:35 | 1769427300 | 2.02 | 7 | 3.5 | 143.5 | 124.22 | 50 | 1 | 0
2026-01-26 06:36 | 1769427360 | 2.02 | 7 | 3.5 | 144.09 | 124.5 | 70 | 1 | 0
2026-01-26 06:37 | 1769427420 | 2.02 | 7 | 3.5 | 144.91 | 124.63 | 98 | 1 | 0
2026-01-26 06:38 | 1769427480 | 2.02 | 7 | 3.5 | 142.92 | 125.13 | 36 | 1 | 0
2026-01-26 06:39 | 1769427540 | 2.02 | 7 | 3.5 | 142.96 | 125.38 | 72 | 1 | 0
2026-01-26 06:40 | 1769427600 | 2.02 | 7 | 3.5 | 144.51 | 125.56 | 82 | 1 | 0
2026-01-26 06:41 | 1769427660 | 2.02 | 7 | 3.5 | 145.91 | 125.6 | 110 | 1 | 0
2026-01-26 06:42 | 1769427720 | 2.02 | 7.5 | 3.5 | 147.23 | 125.9 | 120 | 1 | 0
2026-01-26 06:43 | 1769427780 | 2.02 | 8 | 3.5 | 148.17 | 125.96 | 107 | 1 | 0
2026-01-26 06:44 | 1769427840 | 2.02 | 8 | 3.5 | 148.81 | 126.33 | 117 | 1 | 0
2026-01-26 06:45 | 1769427900 | 2.012 | 8 | 3.5 | 149.47 | 127.01 | 30 | 1 | 0
2026-01-26 06:46 | 1769427960 | 2.01 | 8 | 3.5 | 150.38 | 127.67 | 34 | 1 | 0
2026-01-26 06:47 | 1769428020 | 2.01 | 7.5 | 3.5 | 151.24 | 128.37 | 29 | 1 | 0
2026-01-26 06:48 | 1769428080 | 2.01 | 7 | 3.5 | 151.94 | 128.98 | 35 | 1 | 0
2026-01-26 06:49 | 1769428140 | 2.01 | 7 | 3.5 | 152.71 | 129.56 | 40 | 1 | 0
2026-01-26 06:50 | 1769428200 | 2.01 | 7 | 3.5 | 153.24 | 130.15 | 40 | 1 | 0
2026-01-26 06:51 | 1769428260 | 2.01 | 7 | 3.5 | 153.81 | 130.65 | 33 | 1 | 0
2026-01-26 06:52 | 1769428320 | 2.01 | 7.5 | 3.5 | 154.31 | 131.19 | 44 | 1 | 0
2026-01-26 06:53 | 1769428380 | 2.01 | 8 | 3.5 | 154.75 | 131.69 | 53 | 1 | 0
2026-01-26 06:54 | 1769428440 | 2.01 | 8 | 3.5 | 155.05 | 132.17 | 68 | 1 | 0
2026-01-26 06:55 | 1769428500 | 2.002 | 8 | 3.5 | 155.32 | 132.51 | 78 | 1 | 0
2026-01-26 06:56 | 1769428560 | 2 | 8 | 3.5 | 155.37 | 132.91 | 110 | 1 | 0
2026-01-26 06:57 | 1769428620 | 2 | 8 | 3.5 | 155.62 | 133.22 | 140 | 1 | 0
2026-01-26 06:58 | 1769428680 | 2 | 8 | 3.5 | 156.43 | 133.41 | 82 | 1 | 0
2026-01-26 06:59 | 1769428740 | 2 | 8 | 3.5 | 148.59 | 133.65 | 80 | 1 | 0
2026-01-26 07:00 | 1769428800 | 2.008 | 8 | 3.5 | 147.56 | 133.89 | 90 | 1 | 0
2026-01-26 07:01 | 1769428860 | 2.01 | 8 | 3.5 | 152.56 | 133.01 | 60 | 1 | 0
2026-01-26 07:02 | 1769428920 | 2.01 | 7.5 | 3.5 | 153.01 | 132.37 | 76 | 1 | 0
2026-01-26 07:03 | 1769428980 | 2.01 | 7 | 3.5 | 153.01 | 132.3 | 136 | 1 | 0
2026-01-26 07:04 | 1769429040 | 2.01 | 7 | 3.5 | 152.82 | 131.26 | 166 | 1 | 0
2026-01-26 07:05 | 1769429100 | 2.002 | 7 | 3.5 | 152.64 | 131.07 | 50 | 1 | 0
2026-01-26 07:06 | 1769429160 | 2 | 7 | 3.5 | 152.31 | 131.62 | 60 | 1 | 0
2026-01-26 07:07 | 1769429220 | 2 | 7 | 3.5 | 152.18 | 131.68 | 103 | 1 | 0
2026-01-26 07:08 | 1769429280 | 2 | 7 | 3.5 | 151.82 | 131.68 | 163 | 1 | 0
2026-01-26 07:09 | 1769429340 | 2 | 7 | 3.5 | 151.5 | 131.68 | 223 | 1 | 0
2026-01-26 07:10 | 1769429400 | 2 | 7 | 3.5 | 151.08 | 131.79 | 233 | 1 | 0
2026-01-26 07:11 | 1769429460 | 2 | 7 | 3.5 | 150.7 | 131.81 | 110 | 1 | 0
2026-01-26 07:12 | 1769429520 | 2 | 7 | 3.5 | 150.32 | 131.5 | 120 | 1 | 0
2026-01-26 07:13 | 1769429580 | 2 | 7 | 3.5 | 150.01 | 131.37 | 99 | 1 | 0.333
2026-01-26 07:14 | 1769429640 | 2.88 | 8.3 | 3.5 | 149.61 | 122.67 | 58 | 1 | 1

## beech-cold-zone-events
CallStartEt | CallMinutes | PreDropF | PreSourceF | PostMinutes | RecoveryMin5Pct | RecoveryMin10Pct | PeakExcessF | SourceHeld | AddedGpm | SlugGal
2025-10-10 21:20 | 10 | 6.1 | 92.9 | 34 |  |  | 10.4 | FALSE | 1.93 | 0.4
2025-12-08 01:25 | 6 | 13.2 | 137.5 | 22 |  |  | 22.3 | FALSE | 0.97 | 8.8
2025-12-27 09:22 | 6 | 23.1 | 138.3 | 11 | 7 | 6 | 19.2 | FALSE | 0.73 | 2.3
2025-12-31 04:14 | 7 | 23.3 | 163.5 | 36 |  | 15 | 6.5 | FALSE | 0.91 | 9.1
2025-12-31 12:49 | 6 | 21.9 | 144.1 | 22 |  |  | 23.6 | FALSE | 0.99 | 2.9
2026-01-01 22:45 | 7 | 7.7 | 122.7 | 21 |  |  | 27.7 | FALSE | 0.94 | 5.6
2026-01-02 00:47 | 7 | 23.1 | 161.4 | 14 |  |  | 13.9 | FALSE | 0.93 | 7
2026-01-02 12:20 | 7 | 19.4 | 134.2 | 15 |  |  | 18.5 | FALSE | 0.88 | 2.5
2026-01-04 14:13 | 7 | 27.6 | 158.8 | 11 | 4 | 3 | 20 | FALSE | 0.84 | 3.2
2026-01-05 12:37 | 6 | 20 | 143.3 | 23 | 4 | 1 | 17.9 | FALSE | 1.04 | 4.5
2026-01-05 14:00 | 6 | 28.2 | 173.3 | 11 |  | 6 | 23.2 | TRUE | 0.83 | 4.5
2026-01-16 20:36 | 7 | 24.1 | 152.5 | 10 | 4 | 4 | 18.1 | FALSE | 0.89 | 4.2
2026-01-24 07:35 | 9 | 19.2 | 141.5 | 21 |  | 9 | 4.2 | FALSE | 0.96 | 8.7
2026-01-24 10:16 | 6 | 15.2 | 147.8 | 30 |  |  | 15.2 | FALSE | 0.14 | 2.2
2026-01-24 20:01 | 9 | 14.6 | 130.3 | 26 |  |  | 19.1 | FALSE | 0.91 | 9.2
2026-01-24 20:36 | 8 | 11 | 140.5 | 18 |  |  | 16.7 | FALSE | 0.96 | 10.1
2026-01-25 02:02 | 8 | 22.2 | 149.7 | 15 | 4 | 1 | 15.6 | TRUE | 1 | 5.2
2026-01-25 07:46 | 8 | 10.5 | 134.6 | 21 |  |  | 15.3 | FALSE | 1.03 | 11.2
2026-01-25 08:15 | 8 | 21.2 | 146.4 | 10 | 5 | 1 | 12.3 | TRUE | 1.04 | 4.6
2026-01-25 12:16 | 8 | 20.3 | 139.7 | 13 | 3 | 1 | 12.3 | TRUE | 0.95 | 4.1
2026-01-25 13:05 | 7 | 21.8 | 144.5 | 22 |  |  | 18.4 | FALSE | 1.02 | 3.4
2026-01-25 18:19 | 7 | 12.1 | 133.7 | 10 |  |  | 25.5 | FALSE | 0.96 | 4.5
2026-01-26 02:06 | 7 | 6.4 | 120.2 | 24 |  |  | 25.5 | FALSE | 0.96 | 5.8
2026-01-26 06:17 | 6 | 18.2 | 138.8 | 34 | 5 | 4 | 16.9 | FALSE | 1.06 | 4.2
2026-01-26 21:24 | 6 | 27.2 | 150.4 | 17 | 3 | 3 | 16 | FALSE | 0.97 | 2.3
2026-01-26 22:44 | 7 | 17.6 | 151.5 | 23 |  |  | 22.5 | FALSE | 0.91 | 6.4
2026-01-29 22:38 | 6 | 27.2 | 158.2 | 11 | 4 | 3 | 21.1 | FALSE | 1.04 | 3.1
2026-01-30 05:58 | 6 | 12.8 | 147.4 | 18 |  |  | 24.3 | FALSE | 1.09 | 8.1
2026-01-30 20:30 | 7 | 16 | 129.6 | 15 |  |  | 18.7 | FALSE | 0.97 | 2.9
2026-01-31 01:24 | 8 | 10.8 | 143 | 20 |  |  | 15.9 | FALSE | 0.89 | 11.8
2026-01-31 03:51 | 8 | 18.7 | 142.5 | 10 |  |  | 20.8 | FALSE | 0.87 | 3.4
2026-01-31 04:42 | 7 | 26.1 | 159.5 | 15 |  | 3 | 20 | FALSE | 0.92 | 3.4
2026-01-31 08:35 | 7 | 23.8 | 153 | 15 | 6 | 1 | 16.2 | FALSE | 0.9 | 3.3
2026-01-31 10:37 | 7 | 23.2 | 157.6 | 13 | 9 | 1 | 18.7 | FALSE | 0.93 | 4.9
2026-01-31 22:39 | 7 | 26.6 | 157.7 | 11 | 5 | 3 | 18.3 | FALSE | 0.91 | 3.3
2026-02-01 07:35 | 7 | 19.8 | 142.1 | 16 | 9 | 7 | 16.3 | FALSE | 0.99 | 3.2
2026-02-06 20:29 | 7 | 17.2 | 133.9 | 26 |  |  | 5.5 | FALSE | 0.83 | 7.5
2026-02-06 21:30 | 6 | 22.5 | 155.7 | 13 |  | 8 | 23.1 | FALSE | 0.99 | 4.4
2026-02-07 07:54 | 6 | 20.3 | 150.3 | 27 | 9 | 8 | 19.7 | FALSE | 0.95 | 4.8
2026-02-08 07:34 | 7 | 13.4 | 131.6 | 21 |  |  | 20.4 | FALSE | 0.83 | 4.2
2026-02-09 02:24 | 6 | 20.1 | 154.6 | 23 | 4 | 3 | 26.3 | FALSE | 0.99 | 5.6
2026-02-16 04:54 | 7 | 19.3 | 135.8 | 13 | 10 | 7 | 17.4 | FALSE | 0.85 | 2.6
2026-02-22 00:14 | 7 | 11.4 | 117.4 | 48 |  |  | 17.9 | FALSE | 1.01 | 3.2
2026-02-22 06:39 | 7 | 18.2 | 139.4 | 33 |  | 32 | 14.8 | FALSE | 1 | 6.3
2026-03-02 21:05 | 7 | 15.7 | 133.3 | 16 |  |  | 25.9 | FALSE | 0.93 | 2.6

## beech-cold-zone-excess
MinutesAfter | Events | ShareBeyond3F | MedianExcessF | MedianSourceMoveF | DetrendedQ25F | DetrendedMedianF | DetrendedQ75F | ControlMinutes | ControlShareBeyond3F | ControlDetrendedQ25F | ControlDetrendedMedianF | ControlDetrendedQ75F
10 | 41 | 0.56 | 3.5 | 9.4 | -2.1 | 0.9 | 3.9 | 324 | 0.69 | -2.9 | 0.3 | 6
15 | 26 | 0.73 | 5.6 | 13.2 | -1.1 | 1.8 | 6.1 | 173 | 0.81 | -1 | 2.6 | 6.1
20 | 20 | 0.8 | 3.5 | 12.3 | -2.3 | 0.3 | 2.5 | 98 | 0.84 | -0.3 | 3.3 | 6.3
30 | 5 | 1 | 4.8 | 16.8 | -2.3 | -0.3 | 1.1 | 32 | 0.81 | -1.1 | 1.1 | 3.6

## beech-cold-zone-slug-volume
SlugF | GalQ25 | GalMedian | GalQ75
60 | 2.9 | 4.1 | 5.8
65 | 3.2 | 4.4 | 6.3
70 | 3.5 | 4.7 | 6.9

## beech-steady-drop
System | SourceLoF | SourceHiF | Hours | DropQ25F | DropMedianF | DropQ75F | MedianGpm | MedianKwhPerH
beech | 60 | 70 | 21 | 0.5 | 0.6 | 0.7 | 3.16 | 0.3
beech | 130 | 140 | 29 | 15.8 | 17.1 | 17.7 | 2.1 | 5.18
beech | 140 | 150 | 47 | 19 | 19.8 | 21.2 | 2.1 | 6.11
beech | 150 | 160 | 53 | 21.2 | 23 | 24.4 | 2.1 | 7.1
beech | 160 | 170 | 24 | 24.2 | 25.5 | 26.5 | 2.05 | 7.69